## Slide 1: Fully integrated model of the HES-OFF hybrid system

## Slide 2: Integrated Analysis
Scenario Generation
System Constraints
Analysis & Optimization
Gas Turbine: type, #, MinSP
Wind Turbine: type, #, MaxCurtail
Storage: electrolyzer and fuel cell sizes
Physical: footprint, weight
Power: electrical, thermal
Operational: peak vs. tail, availability
Emissions: CO2, NOx, CO
Storage: capacity
Operational: H2 to GT, curtailed load

## Slide 3: Models integration
The process model (matlab) was succesfully integrated with the offshore grid model (simulink)
The integrated model allows to screen designs in terms of both
  Process performance
  Grid stability
The next step is the design optimization of the HES-OFF concept guided by the dynamic performance of the grid

## Slide 4: Models integration
Energy storage
Proposed design
Design outputs
Run long-term design model
Process the results
Test grid stability with the given design
Inputs to modify the design
NO
YES
Feasible HES-OFF design
SIMULINK MODEL
Dynamic constraints satisfied?

## Slide 5: Hybrid system – long-term design
Inputs to the design
  Power demand during lifetime
  Heat demand during lifetime
  GT (LM2500 vs LM6000)
  GT operation (max/min load)
  Fraction of H2 in GT
  Wind speed data series for North Sea
  Wind turbine (NREL vs Hywind)
  Fuel cell and electrolyser stacks
  H2 storage method
Outputs
  Size of H2 storage
  Size of electrolyser stack
  Size of fuel cell stack
  CO2 emissions
  Weights and footprints
  Costs

## Slide 6: Hybrid system – long-term design
Inputs to the design
  Power demand during lifetime
    43.6/ 35.2/32.9 MW
  Heat demand during lifetime
    15 MW
  GT (LM2500 vs LM6000)
    Both
  GT operation (max/min load)
    95%/40%
  Fraction of H2 in GT
    20% vol.
  Wind speed data series for North Sea
    Sleipner data from the Norwegian Meteorological Institute
  Wind turbine (NREL vs Hywind)
    Hywind
  Fuel cell and electrolyser stacks
    Modelled (see Marcin’s presentation)
  H2 storage method
    Gaseous H2 subsea (see Prototech’s presentation)
Outputs
  Size of H2 storage
  Size of electrolyser stack
  Size of fuel cell stack
  CO2 emissions
  Weights and footprints
  Costs

## Slide 7: Storage strategy
Deficit of power (peak years)
  Evaluate total H2 needed to be used as fuel in the fuel cells
  Whenever possible increase GT load and use extra power to produce H2 in electrolyser
    Stop when reaching a maximum storage level
    Stop when reaching overall H2 needed
Surplus of power (tail years)
  Evaluate H2 produced due to surplus power
  Whenever possible use fuel cells instead of GT
  When the level of storage reaches a maximum, max H2 used in GT
  If not all H2 used, some H2 sent continously to GT during year

## Slide 8: Hybrid system – short-term analysis
Inputs to the analysis
  GT (LM2500 vs LM6000)
  GT operation (max/min load)
  Wind turbine (NREL vs Hywind)
  Fuel cell and electrolyser sizes
  Wind speed variation
    MET Norway data
    Kaimal spectrum
  Power demand variation
    SCADA data Edvard Grieg
    Max load variation = 5.3 MW
Parameters
  GT parameters
    Datasheet from Edvard Grieg
  WT parameters
    Publicly available documents
  GT controllers
    Validated with SCADA data
  ES controllers
    Tuned up following best-practices
Outputs
  Max frequency
  Min frequency
  Max
  Data series of power (GT, WT, ES) and frequency
Long-term design
Statistical analysis
Assumptions

## Slide 9: Some results
INPUTS |  | Only GT | GT + WIND |  |  | GT + WIND + EN STORAGE |  | 
GT |  | LM2500 | LM2500 | LM2500 | LM2500 | LM2500 | LM2500 | LM2500
GT load limits |  | Variable | Variable | Variable | Variable | Variable | Variable | Variable
max GT load | % | 90 % | 90 % | 90 % | 90 % | 95 % | 95 % | 95 %
min GT load | % | 40 % | 40 % | 40 % | 40 % | 40 % | 40 % | 40 %
Wind power capacity | MW | - | 12 | 18 | 24 | 12 | 18 | 24
max H2 in GT |  | - | - | - | - | 0.037 | 0.037 | 0.037
OUTPUTS |  |  |  |  |  |  |  | 
Size of the H2 storage | kg | - | - | - | - | 123883 | 55388 | 70220
Size of the electrolyser stack | MW | - | - | - | - | 4 | 4 | 6
Size of the fuel cell stack | MW | - | - | - | - | 4 | 4 | 4
CO2 emissions | Mt | 3.51 | 2.71 | 2.42 | 2.25 | 2.48 | 2.25 | 2.07
compared to only GT |  | - |  |  |  | -29.2 % | -35.7 % | -40.9 %
compared to GT+wind |  | - |  |  |  | -8.2 % | -6.9 % | -8.0 %
Small GT case:
Good emissions reduction potential
Two GTs with HES-OFF concept
Unfeasible size H2 storage

## Slide 10: Some results
INPUTS |  | Only GT | GT + WIND |  |  | GT + WIND + EN STORAGE |  | 
GT |  | LM2500 | LM2500 | LM2500 | LM2500 | LM2500 | LM2500 | LM2500
GT load limits |  | Variable | Variable | Variable | Variable | Variable | Variable | Variable
max GT load | % | 90 % | 90 % | 90 % | 90 % | 95 % | 95 % | 95 %
min GT load | % | 40 % | 40 % | 40 % | 40 % | 40 % | 40 % | 40 %
Wind power capacity | MW | - | 12 | 18 | 24 | 12 | 18 | 24
Size of the electrolyser | MW | - | - | - | - | 4 | 4 | 6.1
Size of the fuel cell | MW | - | - | - | - | 3.6 | 3.6 | 3.6
OUTPUTS |  |  |  |  |  |  |  | 
Max frequency | Hz | 60.00 | 60.18 | 60.26 | 60.35 | 60.14 | 60.22 | 60.29
Min frequency | Hz | 59.22 | 58.96 | 58.85 | 58.69 | 59.05 | 58.96 | 58.85
GT max dP/dt | % / s | 1.52 | 3.72 | 4.42 | 5.05 | 3.08 | 4.03 | 4.43
Pass NORSOK E-001? | Yes / No | Yes | Yes | Yes | No | Yes | Yes | Yes
compared to rated values | fmax | +0.0 % | +0.3 % | +0.4 % | +0.6 % | +0.2 % | +0.3 % | +0.5
 | fmin | -1.3 % | -1,7% | -1.9 % | -2.2 % | -1.6 % | -1.7 % | -1.9%
Small GT case:
Up to 3 WTs without Storage
Fuel cell allows one additional WT
Reduced range of operation requires 3 GTs to cover spinning reserve and n-1 criteria
When wind power is high, one GT can be left in cold-standby

## Slide 11: Some results
INPUTS |  | Only GT | GT + WIND |  |  | GT + WIND + EN STORAGE |  | 
GT |  | LM6000 | LM6000 | LM6000 | LM6000 | LM6000 | LM6000 | LM6000
GT load limits |  | Variable | Variable | Variable | Variable | Variable | Variable | Variable
max GT load | % | 90 % | 90 % | 90 % | 90 % | 95 % | 95 % | 95 %
min GT load | % | 40 % | 40 % | 40 % | 40 % | 40 % | 40 % | 40 %
Wind power capacity | MW | - | 12 | 18 | 24 | 12 | 18 | 24
max H2 in GT |  | - | - | - | - | 0.037 | 0.037 | 0.037
OUTPUTS |  |  |  |  |  |  |  | 
Size of the H2 storage | kg | - | - | - | - | 7904 | 5876 | 24871
Size of the electrolyser stack | MW | - | - | - | - | 4 | 4 | 9
Size of the fuel cell stack | MW | - | - | - | - | 1 | 1 | 1
CO2 emissions | Mt | 2.92 | 2.48 | 2.36 | 2.30 | 2.45 | 2.31 | 2.21
compared to only GT |  | - |  |  |  | -16.3 % | -20.8 % | -24.4 %
compared to GT+wind |  | - |  |  |  | -1.5 % | -2.0 % | -4.0 %
Big GT case:
More limited emissions reduction
Single GT with HES-OFF concept
Feasible size H2 storage

## Slide 12: Some results
Big GT case:
Up to 3 WTs without Storage
A larger fuel cell allows one additional WT
Increased range of operation requires 2 GTs to cover spinning reserve and n-1 criteria
When wind power is high, one GT can be left in cold-standby
INPUTS |  | Only GT | GT + WIND |  |  | GT + WIND + EN STORAGE |  | 
GT |  | LM6000 | LM6000 | LM6000 | LM6000 | LM6000 | LM6000 | LM6000
GT load limits |  | Variable | Variable | Variable | Variable | Variable | Variable | Variable
max GT load | % | 90 % | 90 % | 90 % | 90 % | 95 % | 95 % | 95 %
min GT load | % | 40 % | 40 % | 40 % | 40 % | 40 % | 40 % | 40 %
Wind power capacity | MW | - | 12 | 18 | 24 | 12 | 18 | 24
Size of the electrolyser | MW | - | - | - | - | 4 | 4 | 6.6
Size of the fuel cell | MW | - | - | - | - | 1.1 | 1.1 | 1.6
OUTPUTS |  |  |  |  |  |  |  | 
Max frequency | Hz | 60.00 | 60.18 | 60.27 | 60.35 | 60.14 | 60.22 | 60.30
Min frequency | Hz | 59.13 | 59.01 | 58.85 | 58.68 | 59.06 | 58.92 | 58.80
GT max dP/dt | % / s | 2.34 | 2.62 | 3.05 | 3.49 | 2.49 | 2.88 | 3.21
Pass NORSOK E-001? | Yes / No | Yes | Yes | Yes | No | Yes | Yes | Yes
compared to rated values | fmax | +0.0 % | +0.3 % | +0.4 % | +0.6 % | +0.2 % | +0.4 % | +0.5
 | fmin | -1.4 % | -1,7% | -1.9 % | -2.2 % | -1.6 % | -1.8 % | -2.0%

## Slide 13: Fuel cell and electrolyser performance
In the first simulations, constant values of fuel cell and electroyser efficiency were used
  Performance electrolyser: 0.007 kg/MJ
  Performance fuel cell: 66 MJ/kg
Models for the fuel cell and for the electrolyser were developed and integrated to the main model for the HES-OFF design
The models return the performance of the fuel cell and of the electrolyser at the specific conditions tested
The stacks are not always run at optimal conditions, thus lower performances are obtained. What is the influence on the design?

## Slide 14: Fuel cell and electrolyser performance
INPUTS |  | Only GT | GT + WIND |  |  | GT + WIND + EN STORAGE |  |  | GT + WIND + EN STORAGE |  | 
GT |  | LM6000 | LM6000 | LM6000 | LM6000 | LM6000 | LM6000 | LM6000 | LM6000 | LM6000 | LM6000
GT load limits |  | Variable | Variable | Variable | Variable | Variable | Variable | Variable | Variable | Variable | Variable
max GT load | % | 90 % | 90 % | 90 % | 90 % | 95 % | 95 % | 95 % | 95 % | 95 % | 95 %
min GT load | % | 40 % | 40 % | 40 % | 40 % | 40 % | 40 % | 40 % | 40 % | 40 % | 40 %
Wind power capacity | MW | - | 12 | 18 | 24 | 12 | 18 | 24 | 12 | 18 | 24
max H2 in GT |  | - | - | - | - | 0.020 | 0.020 | 0.020 | 0.037 | 0.037 | 0.037
FC and EL efficiency |  |  |  |  |  | fixed | fixed | fixed | model | model | model
OUTPUTS |  |  |  |  |  |  |  |  | 26.6 % | 36.4 % | -52.5 %
Size of the H2 storage | kg | - |  |  |  | 7904 | 5876 | 24871 | 10010 | 8014 | 11824
Size of the electrolyser stack | MW | - |  |  |  | 4 | 4 | 9 | 4 | 4 | 7
Size of the fuel cell stack | MW | - |  |  |  | 1 | 1 | 1 | 1 | 1 | 1
CO2 emissions | Mt | 2.92 | 2.48 | 2.36 | 2.30 | 2.45 | 2.31 | 2.21 | 2.45 | 2.32 | 2.23
 |  |  |  |  |  |  |  |  | 0.0 % | 0.2 % | 0.9 %
Need to find a compromise between emission reduction and storage size

## Slide 15: Fuel cell and electrolyser performance
Electrical grid model is not considering restrictions in the operation of fuel cells and electrolysers
However, wind power production might change very fast in low wind speeds
This requires the energy storage system to quickly inject or absorb power to keep a stable grid frequency
A realistic solution must consider an alternative short-term storage
  Supercapacitors
  Variable pressure of reservoir
  Inertia of motors

## Slide 16: Way forward
Refine the integrated model
Develop optimization procedure
Introduce weight and footprint considerations
Constraint the H2 storage size by allowing to waste some wind power
Testing HES-OFF as a short-term energy storage concept (smoothing wind power contribution rather than substituting a GT)
Further develop fuel cell and electrolyser model (Fredrik’s master’s thesis)
Investigate wind data influence on design (Åsmund’s project + additional analyses)

## Slide 17: Way forward
Wind data influence: an example
  LM2500
  Wind farm 18 MW
  Sleipner wind data set
H2 storage size
  55388 kgH2

## Slide 18: Way forward
Wind data influence: an example
  LM2500
  Wind farm 18 MW
  Sleipner wind data set
H2 storage size
  55388 kgH2
Several consecutive hours with low wind
Wind data set used is characterized by an uneven distribution of high wind speed instances and low wind speed instances during the year
HES-OFF design challenge