## Tin_base load
Power | [15 empty] | Power - lower |  | Power - higher |  | HR - lower |  | HR - higher |  | Exh flow - lower |  | Exh flow - higher |  | Exh T - lower |  | Exh T - higher
41.945 |  | T in ( C) |  | Power (MW) |  | HR (kJ/kWh) | Eff |  | Exh flow (kg/s) |  | Exh T (C) |  | T in |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
MW |  | -30 | 1.1907 | 49.944 | 0.96944 | 8479.1013 | 42.46% | 1.1331 | 139.341 | -39.54 | 419.52 |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -29 | 1.1907 | 49.944 | 0.96969 | 8481.2966 | 42.45% | 1.1322 | 139.223 | -38.11 | 420.95 |  | C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Design HR |  | -28 | 1.1907 | 49.944 | 0.96976 | 8481.9001 | 42.44% | 1.1312 | 139.11 | -36.84 | 422.22 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8746.4 |  | -27 | 1.1907 | 49.944 | 0.96984 | 8482.5998 | 42.44% | 1.1303 | 138.991 | -35.54 | 423.52 | Correction factors |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
kJ/kWh |  | -26 | 1.1907 | 49.944 | 0.97096 | 8492.3958 | 42.39% | 1.1322 | 139.2331 | -34.44 | 424.62 |  | 44.707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -25 | 1.1907 | 49.944 | 0.96967 | 8481.1042 | 42.45% | 1.1313 | 139.113 | -34.2 | 424.86 | Power | 1.0658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exhaust flow |  | -24 | 1.1907 | 49.944 | 0.96833 | 8469.4015 | 42.51% | 1.1302 | 138.988 | -33.99 | 425.07 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122.971 |  | -23 | 1.1907 | 49.944 | 0.968 | 8466.4977 | 42.52% | 1.1293 | 138.8691 | -33.02 | 426.04 |  | 8630.3003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
kg/s |  | -22 | 1.1907 | 49.944 | 0.96808 | 8467.1974 | 42.52% | 1.1283 | 138.753 | -31.73 | 427.33 | HR | 0.98673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -21 | 1.1907 | 49.944 | 0.96827 | 8468.903 | 42.51% | 1.1274 | 138.64 | -30.36 | 428.7 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exhaust T |  | -20 | 1.1907 | 49.944 | 0.96826 | 8468.798 | 42.51% | 1.1265 | 138.525 | -29.15 | 429.91 |  | 129.241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
459.06 |  | -19 | 1.1907 | 49.944 | 0.97466 | 8524.8012 | 42.23% | 1.1265 | 138.532 | -23.31 | 435.75 | Exh flow | 1.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
C |  | -18 | 1.1907 | 49.944 | 0.97323 | 8512.3026 | 42.29% | 1.1256 | 138.42 | -23.21 | 435.85 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -17 | 1.1907 | 49.944 | 0.97211 | 8502.4979 | 42.34% | 1.1259 | 138.454 | -23.31 | 435.75 |  | 451.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -16 | 1.1907 | 49.944 | 0.97082 | 8491.1975 | 42.4% | 1.1256 | 138.412 | -23.31 | 435.75 | Exh T | -7.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -15 | 1.1907 | 49.944 | 0.96926 | 8477.5007 | 42.47% | 1.1245 | 138.2781 | -23.24 | 435.82 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -14 | 1.1907 | 49.944 | 0.96771 | 8463.9962 | 42.53% | 1.1232 | 138.1271 | -23.11 | 435.95 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -13 | 1.1907 | 49.944 | 0.96708 | 8458.5035 | 42.56% | 1.1221 | 137.98 | -22.28 | 436.78 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -12 | 1.1907 | 49.944 | 0.96731 | 8460.4977 | 42.55% | 1.1209 | 137.841 | -20.81 | 438.25 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -11 | 1.1907 | 49.944 | 0.96748 | 8462.0021 | 42.54% | 1.1198 | 137.697 | -19.37 | 439.69 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -10 | 1.1907 | 49.944 | 0.96798 | 8466.2965 | 42.52% | 1.1184 | 137.533 | -17.64 | 441.42 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -9 | 1.1902 | 49.921 | 0.96819 | 8468.2033 | 42.51% | 1.1168 | 137.33 | -16.21 | 442.85 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -8 | 1.1837 | 49.65 | 0.96916 | 8476.696 | 42.47% | 1.1138 | 136.966 | -15.79 | 443.27 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -7 | 1.1771 | 49.372 | 0.97013 | 8485.1013 | 42.43% | 1.1108 | 136.594 | -15.43 | 443.63 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -6 | 1.1776 | 49.395 | 0.96972 | 8481.6027 | 42.44% | 1.1136 | 136.941 | -15.77 | 443.29 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -5 | 1.1802 | 49.504 | 0.96894 | 8474.7018 | 42.48% | 1.1182 | 137.503 | -16.33 | 442.73 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -4 | 1.1815 | 49.556 | 0.96851 | 8471.0021 | 42.5% | 1.1217 | 137.936 | -16.69 | 442.37 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -3 | 1.1804 | 49.511 | 0.96868 | 8472.4977 | 42.49% | 1.124 | 138.214 | -16.95 | 442.11 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -2 | 1.1746 | 49.269 | 0.96946 | 8479.3024 | 42.46% | 1.1216 | 137.9221 | -16.69 | 442.37 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | -1 | 1.1657 | 48.896 | 0.97066 | 8489.7981 | 42.4% | 1.1159 | 137.221 | -15.98 | 443.08 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 1.1565 | 48.51 | 0.97198 | 8501.2996 | 42.35% | 1.11 | 136.499 | -15.26 | 443.8 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 1 | 1.1474 | 48.128 | 0.97333 | 8513.0985 | 42.29% | 1.1042 | 135.779 | -14.52 | 444.54 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2 | 1.1383 | 47.748 | 0.97464 | 8524.6 | 42.23% | 1.0983 | 135.062 | -13.8 | 445.26 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 3 | 1.1294 | 47.371 | 0.97598 | 8536.3027 | 42.17% | 1.0925 | 134.3459 | -13.08 | 445.98 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 4 | 1.1203 | 46.993 | 0.97733 | 8548.1016 | 42.11% | 1.0867 | 133.629 | -12.37 | 446.69 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 5 | 1.1113 | 46.613 | 0.97879 | 8560.8976 | 42.05% | 1.0808 | 132.911 | -11.61 | 447.45 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 6 | 1.1022 | 46.231 | 0.98042 | 8575.1018 | 41.98% | 1.075 | 132.19 | -10.76 | 448.3 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 7 | 1.0932 | 45.853 | 0.98189 | 8588.0027 | 41.92% | 1.0691 | 131.471 | -10.02 | 449.04 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 8 | 1.0842 | 45.477 | 0.98352 | 8602.3031 | 41.85% | 1.0633 | 130.754 | -9.18 | 449.88 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 9 | 1.0753 | 45.103 | 0.98502 | 8615.3964 | 41.79% | 1.0575 | 130.038 | -8.44 | 450.62 |  |  | 0 | min | 45.103 | 9 | 0 | 0 | 8615.3964 | 9 | 0 | 0 | 130.038 | 9 | 0 | 0 | 450.62 | 9 | 0 | 0
|  | 10 | 1.0658 | 44.707 | 0.98673 | 8630.3003 | 41.71% | 1.051 | 129.241 | -7.53 | 451.53 |  |  | 1 | min | 0 | 0 | 44.707 | 10 | 0 | 0 | 8630.3003 | 10 | 0 | 0 | 129.241 | 10 | 0 | 0 | 451.53 | 10
|  | 11 | 1.0534 | 44.184 | 0.98894 | 8649.6998 | 41.62% | 1.0412 | 128.041 | -6.16 | 452.9 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 12 | 1.0411 | 43.667 | 0.99121 | 8669.5017 | 41.52% | 1.0316 | 126.8541 | -4.77 | 454.29 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 13 | 1.0278 | 43.112 | 0.99386 | 8692.6971 | 41.41% | 1.0213 | 125.593 | -3.26 | 455.8 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 14 | 1.0141 | 42.538 | 0.99681 | 8718.499 | 41.29% | 1.0109 | 124.314 | -1.7 | 457.36 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| design | 15 | 1 | 41.945 | 1 | 8746.4 | 41.16% | 1 | 122.971 | 0 | 459.06 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 16 | 0.98682 | 41.392 | 1.0029 | 8772.0969 | 41.04% | 0.99001 | 121.743 | 1.48 | 460.54 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 17 | 0.97425 | 40.865 | 1.006 | 8798.7035 | 40.92% | 0.98052 | 120.575 | 3.04 | 462.1 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 18 | 0.96183 | 40.344 | 1.0089 | 8824.1992 | 40.8% | 0.97111 | 119.418 | 4.48 | 463.54 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 19 | 0.94753 | 39.744 | 1.0122 | 8853.2023 | 40.66% | 0.96079 | 118.1491 | 5.72 | 464.78 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 20 | 0.93267 | 39.121 | 1.0161 | 8887.1033 | 40.51% | 0.95023 | 116.851 | 7.15 | 466.21 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 21 | 0.91832 | 38.519 | 1.0197 | 8918.8003 | 40.36% | 0.93998 | 115.59 | 8.41 | 467.47 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 22 | 0.90049 | 37.771 | 1.0247 | 8962.6985 | 40.17% | 0.92819 | 114.1409 | 9.65 | 468.71 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 23 | 0.88978 | 37.322 | 1.0269 | 8982.0018 | 40.08% | 0.91904 | 113.015 | 10.95 | 470.01 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 24 | 0.87827 | 36.839 | 1.0295 | 9004.6987 | 39.98% | 0.90931 | 111.819 | 12.36 | 471.42 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 25 | 0.86725 | 36.377 | 1.0324 | 9029.5997 | 39.87% | 0.89964 | 110.63 | 14.12 | 473.18 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 26 | 0.85686 | 35.941 | 1.0348 | 9050.8972 | 39.78% | 0.89034 | 109.486 | 15.69 | 474.75 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 27 | 0.84644 | 35.504 | 1.0374 | 9073.9002 | 39.67% | 0.88154 | 108.404 | 17.1 | 476.16 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 28 | 0.83562 | 35.05 | 1.0401 | 9097.4018 | 39.57% | 0.87364 | 107.432 | 17.88 | 476.94 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 29 | 0.8252 | 34.613 | 1.043 | 9122.3028 | 39.46% | 0.86588 | 106.478 | 18.84 | 477.9 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 30 | 0.81516 | 34.192 | 1.0455 | 9144.5974 | 39.37% | 0.85825 | 105.54 | 19.67 | 478.73 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 31 | 0.80553 | 33.788 | 1.0479 | 9165.0027 | 39.28% | 0.8508 | 104.624 | 20.42 | 479.48 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 32 | 0.79592 | 33.385 | 1.0505 | 9187.997 | 39.18% | 0.84335 | 103.708 | 21.35 | 480.41 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 33 | 0.78675 | 33 | 1.0532 | 9211.6997 | 39.08% | 0.83608 | 102.814 | 22.39 | 481.45 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 34 | 0.77766 | 32.619 | 1.0558 | 9234.7028 | 38.98% | 0.82876 | 101.913 | 23.42 | 482.48 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 35 | 0.76791 | 32.21 | 1.0589 | 9261.7991 | 38.87% | 0.82001 | 100.8379 | 25.05 | 484.11 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 36 | 0.75852 | 31.816 | 1.0622 | 9290.601 | 38.75% | 0.81142 | 99.781 | 26.9 | 485.96 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 37 | 0.74939 | 31.433 | 1.0654 | 9318.3009 | 38.63% | 0.80283 | 98.7251 | 28.76 | 487.82 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 38 | 0.74126 | 31.092 | 1.0682 | 9343.2981 | 38.53% | 0.7937 | 97.602 | 31.19 | 490.25 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 39 | 0.73379 | 30.779 | 1.0714 | 9370.4994 | 38.42% | 0.7833 | 96.3231 | 34.86 | 493.92 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 40 | 0.72562 | 30.436 | 1.0751 | 9403.2022 | 38.28% | 0.77197 | 94.93 | 39.03 | 498.09 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 41 | 0.6993 | 29.332 | 1.0851 | 9490.7974 | 37.93% | 0.74729 | 91.895 | 43.87 | 502.93 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 42 | 0.69491 | 29.148 | 1.087 | 9506.8995 | 37.87% | 0.74373 | 91.457 | 44.67 | 503.73 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 43 | 0.69055 | 28.965 | 1.0888 | 9523.0016 | 37.8% | 0.74016 | 91.018 | 45.46 | 504.52 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 44 | 0.68618 | 28.782 | 1.0907 | 9539.2961 | 37.74% | 0.73655 | 90.574 | 46.24 | 505.3 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 45 | 0.68161 | 28.59 | 1.0929 | 9558.5032 | 37.66% | 0.73281 | 90.115 | 47.13 | 506.19 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 46 | 0.67705 | 28.399 | 1.0951 | 9577.7978 | 37.59% | 0.72907 | 89.654 | 48.01 | 507.07 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 47 | 0.66952 | 28.083 | 1.0983 | 9605.8038 | 37.48% | 0.72456 | 89.1 | 48.03 | 507.09 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 48 | 0.66122 | 27.735 | 1.102 | 9638.1042 | 37.35% | 0.71982 | 88.517 | 47.9 | 506.96 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 45.103 | 9 | 44.707 | 10 | 8615.3964 | 9 | 8630.3003 | 10 | 130.038 | 9 | 129.241 | 10 | 450.62 | 9 | 451.53 | 10

## Patm_base load
Power | [15 empty] | Power - lower |  | Power - higher |  | HR - lower |  | HR - higher |  | Exh flow - lower |  | Exh flow - higher |  | Exh T - lower |  | Exh T - higher
41.945 |  | P in (bar) |  | Power (MW) |  | HR (kJ/kWh) | Eff |  | Exh flow (kg/s) |  | Exh T (C) |  | P atm |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
MW |  | 0.85897 | 0.83533 | 35.038 | 1.0066 | 8803.6977 | 40.89% | 0.83966 | 103.254 | 1.7 | 460.76 |  | 1.0132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.86218 | 0.83879 | 35.183 | 1.0064 | 8802.7006 | 40.9% | 0.84306 | 103.6721 | 1.7 | 460.76 |  | bar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Design HR |  | 0.8654 | 0.84225 | 35.328 | 1.0062 | 8800.6977 | 40.91% | 0.84639 | 104.0811 | 1.61 | 460.67 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8746.4 |  | 0.86862 | 0.84577 | 35.476 | 1.0061 | 8799.4032 | 40.91% | 0.84984 | 104.5051 | 1.59 | 460.65 | Correction factors |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
kJ/kWh |  | 0.87186 | 0.84923 | 35.621 | 1.0059 | 8798.0038 | 40.92% | 0.85321 | 104.92 | 1.55 | 460.61 |  | 41.945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.87511 | 0.85281 | 35.771 | 1.0057 | 8796.202 | 40.93% | 0.85663 | 105.341 | 1.5 | 460.56 | Power | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exhaust flow |  | 0.87836 | 0.85634 | 35.919 | 1.0056 | 8795.0037 | 40.93% | 0.86006 | 105.7619 | 1.48 | 460.54 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122.971 |  | 0.88163 | 0.85989 | 36.068 | 1.0054 | 8793.202 | 40.94% | 0.86348 | 106.183 | 1.43 | 460.49 |  | 8746.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
kg/s |  | 0.88491 | 0.86339 | 36.215 | 1.0052 | 8791.8026 | 40.95% | 0.86691 | 106.605 | 1.37 | 460.43 | HR | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.8882 | 0.86699 | 36.366 | 1.005 | 8790.0008 | 40.96% | 0.87038 | 107.031 | 1.32 | 460.38 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exhaust T |  | 0.89149 | 0.87062 | 36.518 | 1.0048 | 8788.4002 | 40.96% | 0.87386 | 107.4589 | 1.28 | 460.34 |  | 122.971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
459.06 |  | 0.89479 | 0.87407 | 36.663 | 1.0047 | 8787.4031 | 40.97% | 0.8773 | 107.882 | 1.23 | 460.29 | Exh flow | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
C |  | 0.89811 | 0.87767 | 36.814 | 1.0045 | 8785.8987 | 40.97% | 0.88079 | 108.311 | 1.2 | 460.26 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.90143 | 0.88135 | 36.968 | 1.0043 | 8784.0008 | 40.98% | 0.88429 | 108.742 | 1.14 | 460.2 |  | 459.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.90477 | 0.88492 | 37.118 | 1.0042 | 8782.6976 | 40.99% | 0.8878 | 109.173 | 1.1 | 460.16 | Exh T | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.90812 | 0.88859 | 37.272 | 1.004 | 8781.2019 | 41% | 0.89132 | 109.607 | 1.06 | 460.12 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.91147 | 0.89229 | 37.427 | 1.0037 | 8779.1028 | 41.01% | 0.89485 | 110.04 | 0.99 | 460.05 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.91484 | 0.89598 | 37.582 | 1.0035 | 8777.1961 | 41.02% | 0.89838 | 110.4751 | 0.93 | 459.99 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.91822 | 0.89956 | 37.732 | 1.0034 | 8776.1028 | 41.02% | 0.90191 | 110.909 | 0.89 | 459.95 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.9216 | 0.90328 | 37.888 | 1.0032 | 8774.301 | 41.03% | 0.90547 | 111.347 | 0.83 | 459.89 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.925 | 0.90695 | 38.042 | 1.0031 | 8773.1028 | 41.03% | 0.90906 | 111.788 | 0.8 | 459.86 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.92841 | 0.91055 | 38.193 | 1.003 | 8772.2019 | 41.04% | 0.91261 | 112.2251 | 0.77 | 459.83 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.93182 | 0.91413 | 38.343 | 1.0028 | 8771.196 | 41.04% | 0.91613 | 112.6571 | 0.74 | 459.8 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.93525 | 0.91775 | 38.495 | 1.0027 | 8769.7966 | 41.05% | 0.91965 | 113.09 | 0.69 | 459.75 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.93869 | 0.92142 | 38.649 | 1.0025 | 8768.3972 | 41.06% | 0.9232 | 113.527 | 0.65 | 459.71 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.94213 | 0.92483 | 38.792 | 1.0025 | 8768.5022 | 41.06% | 0.92668 | 113.955 | 0.64 | 459.7 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.94559 | 0.92881 | 38.959 | 1.0022 | 8765.301 | 41.07% | 0.93032 | 114.402 | 0.56 | 459.62 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.94906 | 0.93239 | 39.109 | 1.0021 | 8764.6013 | 41.07% | 0.93387 | 114.8391 | 0.53 | 459.59 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.95253 | 0.93596 | 39.259 | 1.002 | 8764.1027 | 41.08% | 0.93744 | 115.2781 | 0.52 | 459.58 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.95602 | 0.9398 | 39.42 | 1.0018 | 8762.0998 | 41.09% | 0.94107 | 115.724 | 0.46 | 459.52 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.95952 | 0.94324 | 39.564 | 1.0019 | 8763.403 | 41.08% | 0.94462 | 116.161 | 0.54 | 459.6 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.96303 | 0.94688 | 39.717 | 1.0017 | 8761.4001 | 41.09% | 0.94821 | 116.602 | 0.43 | 459.49 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.96655 | 0.95082 | 39.882 | 1.0014 | 8759.0036 | 41.1% | 0.95188 | 117.053 | 0.36 | 459.42 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.97008 | 0.95451 | 40.037 | 1.0013 | 8757.9977 | 41.11% | 0.95551 | 117.5 | 0.33 | 459.39 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.97362 | 0.9583 | 40.196 | 1.0012 | 8756.7033 | 41.11% | 0.95917 | 117.95 | 0.29 | 459.35 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.97717 | 0.96205 | 40.353 | 1.0011 | 8755.6012 | 41.12% | 0.96283 | 118.4 | 0.26 | 459.32 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.98073 | 0.96588 | 40.514 | 1.0009 | 8753.8957 | 41.12% | 0.96651 | 118.8529 | 0.2 | 459.26 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.9843 | 0.96951 | 40.666 | 1.0008 | 8753.7032 | 41.13% | 0.97016 | 119.302 | 0.19 | 459.25 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.98788 | 0.97313 | 40.818 | 1.0009 | 8754.298 | 41.12% | 0.97381 | 119.751 | 0.25 | 459.31 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.99147 | 0.97714 | 40.986 | 1.0005 | 8751.0968 | 41.14% | 0.97756 | 120.212 | 0.12 | 459.18 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.99508 | 0.98078 | 41.139 | 1.0006 | 8751.7965 | 41.13% | 0.98127 | 120.668 | 0.16 | 459.22 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0.99869 | 0.98453 | 41.296 | 1.0004 | 8750.3009 | 41.14% | 0.98495 | 121.12 | 0.08 | 459.14 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 1.0023 | 0.98841 | 41.459 | 1.0004 | 8749.4962 | 41.15% | 0.98872 | 121.584 | 0.08 | 459.14 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 1.0059 | 0.99223 | 41.619 | 1.0002 | 8748.0968 | 41.15% | 0.99245 | 122.042 | 0.02 | 459.08 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 1.0096 | 0.99611 | 41.782 | 1.0001 | 8747.5983 | 41.15% | 0.99622 | 122.506 | 0.04 | 459.1 |  |  | 0 | min | 41.782 | 1.0096 | 0 | 0 | 8747.5983 | 1.0096 | 0 | 0 | 122.506 | 1.0096 | 0 | 0 | 459.1 | 1.0096 | 0 | 0
| design | 1.0132 | 1 | 41.945 | 1 | 8746.4 | 41.16% | 1 | 122.971 | 0 | 459.06 |  |  | 1 | min | 0 | 0 | 41.945 | 1.0132 | 0 | 0 | 8746.4 | 1.0132 | 0 | 0 | 122.971 | 1.0132 | 0 | 0 | 459.06 | 1.0132
|  | 1.0169 | 1.0037 | 42.1 | 0.99987 | 8745.298 | 41.16% | 1.0037 | 123.425 | -0.07 | 458.99 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 1.0206 | 1.0075 | 42.259 | 0.99977 | 8744.3971 | 41.17% | 1.0074 | 123.8841 | -0.11 | 458.95 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 1.0243 | 1.0114 | 42.424 | 0.99959 | 8742.7965 | 41.18% | 1.0112 | 124.347 | -0.15 | 458.91 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 1.028 | 1.0151 | 42.579 | 0.99969 | 8743.6974 | 41.17% | 1.0149 | 124.807 | -0.08 | 458.98 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 1.0317 | 1.019 | 42.74 | 0.9995 | 8742.0006 | 41.18% | 1.0187 | 125.2699 | -0.18 | 458.88 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 41.782 | 1.0096 | 41.945 | 1.0132 | 8747.5983 | 1.0096 | 8746.4 | 1.0132 | 122.506 | 1.0096 | 122.971 | 1.0132 | 459.1 | 1.0096 | 459.06 | 1.0132

## DP in_base load
Power | [14 empty] | Power - lower |  | Power - higher |  | HR - lower |  | HR - higher |  | Exh flow - lower |  | Exh flow - higher |  | Exh T - lower |  | Exh T - higher
41.945 | DP in ( C) |  | Power (MW) |  | HR (kJ/kWh) | Eff |  | Exh flow (kg/s) |  | Exh T (C) |  | DP in |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
MW | 0 | 1.0146 | 42.558 | 0.9952 | 8704.3998 | 41.36% | 1.0097 | 124.158 | -1.43 | 457.63 |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.25 | 1.0128 | 42.48 | 0.99571 | 8708.9042 | 41.34% | 1.0084 | 124.009 | -1.3 | 457.76 |  | mbar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Design HR | 2.49 | 1.011 | 42.406 | 0.99632 | 8714.1958 | 41.31% | 1.0073 | 123.871 | -1.13 | 457.93 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8746.4 | 3.74 | 1.0094 | 42.338 | 0.99684 | 8718.7964 | 41.29% | 1.0062 | 123.7319 | -0.95 | 458.11 | Correction factors |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
kJ/kWh | 4.98 | 1.0072 | 42.249 | 0.99754 | 8724.9013 | 41.26% | 1.0048 | 123.562 | -0.76 | 458.3 |  | 41.9424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.23 | 1.0054 | 42.173 | 0.99814 | 8730.0967 | 41.24% | 1.0036 | 123.4139 | -0.58 | 458.48 | Power | 0.99994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exhaust flow | 7.47 | 1.0036 | 42.095 | 0.99875 | 8735.502 | 41.21% | 1.0024 | 123.264 | -0.4 | 458.66 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122.971 | 8.72 | 1.0018 | 42.019 | 0.9994 | 8741.1959 | 41.18% | 1.0012 | 123.117 | -0.19 | 458.87 |  | 8746.5601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
kg/s | 9.96 | 1 | 41.945 | 1 | 8746.4 | 41.16% | 1 | 122.971 | 0 | 459.06 | HR | 1 | 0 | min | 41.945 | 9.96 | 0 | 0 | 8746.4 | 9.96 | 0 | 0 | 122.971 | 9.96 | 0 | 0 | 459.06 | 9.96 | 0 | 0
| 11.21 | 0.99809 | 41.865 | 1.0006 | 8751.4029 | 41.14% | 0.99875 | 122.817 | 0.14 | 459.2 |  |  | 1 | min | 0 | 0 | 41.865 | 11.21 | 0 | 0 | 8751.4029 | 11.21 | 0 | 0 | 122.817 | 11.21 | 0 | 0 | 459.2 | 11.21
Exhaust T | 12.45 | 0.99628 | 41.789 | 1.0012 | 8756.7033 | 41.11% | 0.99755 | 122.67 | 0.31 | 459.37 |  | 122.9661 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
459.06 | 13.7 | 0.99447 | 41.713 | 1.0019 | 8762.7995 | 41.08% | 0.99635 | 122.522 | 0.56 | 459.62 | Exh flow | 0.99996 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
C | 14.95 | 0.99261 | 41.635 | 1.0024 | 8767.6013 | 41.06% | 0.99511 | 122.37 | 0.69 | 459.75 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 16.19 | 0.99075 | 41.557 | 1.003 | 8772.9978 | 41.04% | 0.99389 | 122.219 | 0.87 | 459.93 |  | 459.0645 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 17.44 | 0.98894 | 41.481 | 1.0037 | 8778.6042 | 41.01% | 0.99267 | 122.07 | 1.06 | 460.12 | Exh T | 0.00448 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 18.68 | 0.9871 | 41.404 | 1.0043 | 8784.097 | 40.98% | 0.99147 | 121.9221 | 1.24 | 460.3 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 19.93 | 0.98524 | 41.326 | 1.005 | 8789.7034 | 40.96% | 0.99026 | 121.773 | 1.43 | 460.49 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 21.17 | 0.98338 | 41.248 | 1.0056 | 8795.1962 | 40.93% | 0.98903 | 121.622 | 1.61 | 460.67 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 22.42 | 0.98155 | 41.171 | 1.0062 | 8800.8988 | 40.9% | 0.98781 | 121.472 | 1.8 | 460.86 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 23.66 | 0.97971 | 41.094 | 1.007 | 8807.1962 | 40.88% | 0.98661 | 121.324 | 2.04 | 461.1 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 24.91 | 0.97788 | 41.017 | 1.0076 | 8812.6977 | 40.85% | 0.98539 | 121.174 | 2.22 | 461.28 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 26.15 | 0.97602 | 40.939 | 1.0082 | 8818.4004 | 40.82% | 0.98417 | 121.024 | 2.41 | 461.47 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 27.4 | 0.97418 | 40.862 | 1.0089 | 8824.1992 | 40.8% | 0.98295 | 120.874 | 2.61 | 461.67 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 28.65 | 0.97232 | 40.784 | 1.0095 | 8829.5958 | 40.77% | 0.98172 | 120.723 | 2.77 | 461.83 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 29.89 | 0.97049 | 40.707 | 1.0102 | 8835.5958 | 40.74% | 0.9805 | 120.5729 | 2.98 | 462.04 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 31.14 | 0.96865 | 40.63 | 1.0108 | 8841.0973 | 40.72% | 0.97928 | 120.423 | 3.15 | 462.21 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 32.38 | 0.96643 | 40.537 | 1.0117 | 8848.4005 | 40.69% | 0.97789 | 120.252 | 3.4 | 462.46 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 33.63 | 0.96495 | 40.475 | 1.0122 | 8852.7037 | 40.67% | 0.97684 | 120.123 | 3.54 | 462.6 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 34.87 | 0.9631 | 40.397 | 1.0128 | 8858.1965 | 40.64% | 0.9756 | 119.97 | 3.71 | 462.77 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 36.12 | 0.96126 | 40.32 | 1.0135 | 8864.3977 | 40.61% | 0.97438 | 119.821 | 3.94 | 463 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 37.36 | 0.95949 | 40.246 | 1.0141 | 8869.803 | 40.59% | 0.97322 | 119.678 | 4.1 | 463.16 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 38.61 | 0.95761 | 40.167 | 1.0148 | 8875.4969 | 40.56% | 0.97198 | 119.526 | 4.28 | 463.34 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 39.85 | 0.9559 | 40.095 | 1.0153 | 8880.2986 | 40.54% | 0.97081 | 119.381 | 4.42 | 463.48 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 41.1 | 0.95387 | 40.01 | 1.0161 | 8887.1033 | 40.51% | 0.96946 | 119.215 | 4.65 | 463.71 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 42.35 | 0.95203 | 39.933 | 1.0168 | 8893.1996 | 40.48% | 0.96825 | 119.0661 | 4.87 | 463.93 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 43.59 | 0.95017 | 39.855 | 1.0175 | 8899.2958 | 40.45% | 0.967 | 118.913 | 5.07 | 464.13 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 44.84 | 0.94834 | 39.778 | 1.0182 | 8905.1996 | 40.43% | 0.96578 | 118.7631 | 5.26 | 464.32 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 46.08 | 0.94648 | 39.7 | 1.0188 | 8911.1997 | 40.4% | 0.96454 | 118.6109 | 5.46 | 464.52 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 47.33 | 0.94469 | 39.625 | 1.0194 | 8916.2988 | 40.38% | 0.96337 | 118.466 | 5.59 | 464.65 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 48.57 | 0.9429 | 39.55 | 1.0201 | 8922.5 | 40.35% | 0.96217 | 118.319 | 5.81 | 464.87 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 49.82 | 0.94097 | 39.469 | 1.0208 | 8928.7012 | 40.32% | 0.96086 | 118.158 | 6.01 | 465.07 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | 41.945 | 9.96 | 41.865 | 11.21 | 8746.4 | 9.96 | 8751.4029 | 11.21 | 122.971 | 9.96 | 122.817 | 11.21 | 459.06 | 9.96 | 459.2 | 11.21

## DP out_base load
Power | [13 empty] | Power - lower |  | Power - higher |  | HR - lower |  | HR - higher |  | Exh flow - lower |  | Exh flow - higher |  | Exh T - lower |  | Exh T - higher
41.945 | DP in ( C) |  | Power (MW) |  | HR (kJ/kWh) | Eff | Exh flow (kg/s) |  | Exh T (C) |  | DP out |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
MW | 0 | 1.0076 | 42.264 | 0.99268 | 8682.4026 | 41.46% | 0 | -2.27 | 456.79 |  | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1.25 | 1.007 | 42.237 | 0.99328 | 8687.598 | 41.44% | 0 | -2.09 | 456.97 |  | mbar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Design HR | 2.49 | 1.0063 | 42.21 | 0.99389 | 8693.0032 | 41.41% | 0 | -1.9 | 457.16 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8746.4 | 3.74 | 1.0057 | 42.184 | 0.99452 | 8698.496 | 41.39% | 0 | -1.69 | 457.37 | Correction factors |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
kJ/kWh | 4.98 | 1.0051 | 42.157 | 0.99512 | 8703.7001 | 41.36% | 0 | -1.51 | 457.55 |  | 41.9439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.23 | 1.0044 | 42.13 | 0.99577 | 8709.4027 | 41.33% | 0 | -1.3 | 457.76 | Power | 0.99997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exhaust flow | 7.47 | 1.0038 | 42.103 | 0.99638 | 8714.703 | 41.31% | 0 | -1.11 | 457.95 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122.971 | 8.72 | 1.0031 | 42.076 | 0.99696 | 8719.8022 | 41.29% | 0 | -0.94 | 458.12 |  | 8746.6218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
kg/s | 9.96 | 1.0025 | 42.05 | 0.99758 | 8725.1987 | 41.26% | 0 | -0.75 | 458.31 | HR | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 11.21 | 1.0019 | 42.023 | 0.99817 | 8730.4028 | 41.24% | 0 | -0.57 | 458.49 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exhaust T | 12.45 | 1.0012 | 41.996 | 0.99878 | 8735.7032 | 41.21% | 0 | -0.39 | 458.67 |  | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
459.06 | 13.7 | 1.0006 | 41.97 | 0.9994 | 8741.1959 | 41.18% | 0 | -0.19 | 458.87 | Exh flow | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
C | 14.95 | 1 | 41.945 | 1 | 8746.4 | 41.16% | 0 | 0 | 459.06 |  |  | 0 | min | 41.945 | 14.95 | 0 | 0 | 8746.4 | 14.95 | 0 | 0 | 0 | 0 | 0 | 0 | 459.06 | 14.95 | 0 | 0
| 16.19 | 0.99933 | 41.917 | 1.0006 | 8751.9015 | 41.13% | 0 | 0.2 | 459.26 |  | 459.0681 | 1 | min | 0 | 0 | 41.917 | 16.19 | 0 | 0 | 8751.9015 | 16.19 | 0 | 0 | 0 | 0 | 0 | 0 | 459.26 | 16.19
| 17.44 | 0.99867 | 41.889 | 1.0012 | 8757.0006 | 41.11% | 0 | 0.35 | 459.41 | Exh T | 0.0080645 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 18.68 | 0.99802 | 41.862 | 1.0018 | 8762.301 | 41.09% | 0 | 0.54 | 459.6 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 19.93 | 0.99738 | 41.835 | 1.0024 | 8767.3039 | 41.06% | 0 | 0.69 | 459.75 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 21.17 | 0.99681 | 41.811 | 1.0031 | 8773.3039 | 41.03% | 0 | 0.94 | 460 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 22.42 | 0.99611 | 41.782 | 1.0036 | 8778.0007 | 41.01% | 0 | 1.06 | 460.12 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 23.66 | 0.99547 | 41.755 | 1.0043 | 8784.2019 | 40.98% | 0 | 1.31 | 460.37 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 24.91 | 0.9948 | 41.727 | 1.0049 | 8789.0999 | 40.96% | 0 | 1.46 | 460.52 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 26.15 | 0.99418 | 41.701 | 1.0055 | 8794.8988 | 40.93% | 0 | 1.68 | 460.74 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 27.4 | 0.99354 | 41.674 | 1.0062 | 8800.4003 | 40.91% | 0 | 1.86 | 460.92 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 28.65 | 0.99289 | 41.647 | 1.0068 | 8805.7968 | 40.88% | 0 | 2.04 | 461.1 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 29.89 | 0.99223 | 41.619 | 1.0074 | 8811.0971 | 40.86% | 0 | 2.23 | 461.29 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 31.14 | 0.99161 | 41.593 | 1.008 | 8816.5024 | 40.83% | 0 | 2.41 | 461.47 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 32.38 | 0.99094 | 41.565 | 1.0086 | 8822.0039 | 40.81% | 0 | 2.6 | 461.66 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 33.63 | 0.9903 | 41.538 | 1.0093 | 8827.6016 | 40.78% | 0 | 2.79 | 461.85 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 34.87 | 0.98965 | 41.511 | 1.0098 | 8832.4996 | 40.76% | 0 | 2.94 | 462 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 36.12 | 0.98899 | 41.483 | 1.0105 | 8838.001 | 40.73% | 0 | 3.12 | 462.18 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 37.36 | 0.98837 | 41.457 | 1.0111 | 8843.3014 | 40.71% | 0 | 3.3 | 462.36 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 38.61 | 0.98772 | 41.43 | 1.0117 | 8848.6979 | 40.68% | 0 | 3.48 | 462.54 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 39.85 | 0.98708 | 41.403 | 1.0123 | 8854.1994 | 40.66% | 0 | 3.67 | 462.73 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 41.1 | 0.98646 | 41.377 | 1.0129 | 8859.5959 | 40.63% | 0 | 3.86 | 462.92 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 42.35 | 0.98581 | 41.35 | 1.0136 | 8865.0012 | 40.61% | 0 | 4.03 | 463.09 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 43.59 | 0.98517 | 41.323 | 1.0142 | 8870.3977 | 40.58% | 0 | 4.22 | 463.28 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 44.84 | 0.98453 | 41.296 | 1.0148 | 8875.8992 | 40.56% | 0 | 4.41 | 463.47 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 46.08 | 0.98388 | 41.269 | 1.0154 | 8881.2957 | 40.53% | 0 | 4.59 | 463.65 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 47.33 | 0.98326 | 41.243 | 1.0161 | 8886.7972 | 40.51% | 0 | 4.77 | 463.83 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 48.57 | 0.98262 | 41.216 | 1.0167 | 8892.0975 | 40.49% | 0 | 4.95 | 464.01 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 49.82 | 0.982 | 41.19 | 1.0173 | 8897.599 | 40.46% | 0 | 5.13 | 464.19 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 51.06 | 0.98138 | 41.164 | 1.0179 | 8903.0043 | 40.44% | 0 | 5.31 | 464.37 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 52.31 | 0.98071 | 41.136 | 1.0185 | 8908.497 | 40.41% | 0 | 5.5 | 464.56 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 53.55 | 0.98007 | 41.109 | 1.0192 | 8913.9023 | 40.39% | 0 | 5.67 | 464.73 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 54.8 | 0.97947 | 41.084 | 1.0198 | 8919.4038 | 40.36% | 0 | 5.87 | 464.93 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 56.05 | 0.97883 | 41.057 | 1.0205 | 8925.5 | 40.33% | 0 | 6.1 | 465.16 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 57.29 | 0.97819 | 41.03 | 1.021 | 8930.1968 | 40.31% | 0 | 6.21 | 465.27 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 58.54 | 0.97754 | 41.003 | 1.0216 | 8935.6983 | 40.29% | 0 | 6.4 | 465.46 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 59.78 | 0.97695 | 40.978 | 1.0224 | 8941.8995 | 40.26% | 0 | 6.64 | 465.7 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 61.03 | 0.9763 | 40.951 | 1.023 | 8947.401 | 40.24% | 0 | 6.82 | 465.88 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 62.27 | 0.97566 | 40.924 | 1.0236 | 8952.9025 | 40.21% | 0 | 7 | 466.06 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 63.52 | 0.97504 | 40.898 | 1.0242 | 8958.299 | 40.19% | 0 | 7.18 | 466.24 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 64.76 | 0.9744 | 40.871 | 1.0249 | 8963.8005 | 40.16% | 0 | 7.37 | 466.43 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 66.01 | 0.97377 | 40.845 | 1.0255 | 8969.197 | 40.14% | 0 | 7.55 | 466.61 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 67.25 | 0.97313 | 40.818 | 1.0261 | 8974.8035 | 40.11% | 0 | 7.73 | 466.79 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 68.5 | 0.97254 | 40.793 | 1.0267 | 8980.2 | 40.09% | 0 | 7.9 | 466.96 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 69.74 | 0.97189 | 40.766 | 1.0273 | 8985.5965 | 40.06% | 0 | 8.08 | 467.14 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 70.99 | 0.97125 | 40.739 | 1.028 | 8991.098 | 40.04% | 0 | 8.26 | 467.32 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 72.24 | 0.97063 | 40.713 | 1.0286 | 8996.5033 | 40.02% | 0 | 8.44 | 467.5 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 73.48 | 0.97001 | 40.687 | 1.0292 | 9001.996 | 39.99% | 0 | 8.61 | 467.67 |  |  | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 74.73 | 0.96939 | 40.661 | 1.0298 | 9007.4013 | 39.97% | 0 | 8.79 | 467.85 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[14 empty] | 41.945 | 14.95 | 41.917 | 16.19 | 8746.4 | 14.95 | 8751.9015 | 16.19 | 0 | 0 | 0 | 0 | 459.06 | 14.95 | 459.26 | 16.19

## Part-load_HR_Tin
Inlet Temp | -20 | C |  | Inlet Temp | -15 | C |  | Inlet Temp | -10 | C |  | Inlet Temp | -5 | C |  | Inlet Temp | 0 | C |  | Inlet Temp | 5 | C |  | Inlet Temp | 10 | C |  | Inlet Temp | 15 | C |  | Inlet Temp | 20 | C |  | Inlet Temp | 25 | C
HR | 8468.798 | kJ/kWh |  | HR | 8477.5007 | kJ/kWh |  | HR | 8466.2965 | kJ/kWh |  | HR | 8474.7018 | kJ/kWh |  | HR | 8501.2996 | kJ/kWh |  | HR | 8560.8976 | kJ/kWh |  | HR | 8630.3003 | kJ/kWh |  | HR | 8746.4 | kJ/kWh |  | HR | 8887.1033 | kJ/kWh |  | HR | 9029.5997 | kJ/kWh | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | X | 0 | 0
[40 empty] | T in | 10 | C |  | low | -20 | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20
[40 empty] | Part load | 90% |  |  | high | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25
Part load |  | HR (kJ/kWh) | Eff | Part load |  | HR (kJ/kWh) | Eff | Part load |  | HR (kJ/kWh) | Eff | Part load |  | HR (kJ/kWh) | Eff | Part load |  | HR (kJ/kWh) | Eff | Part load |  | HR (kJ/kWh) | Eff | Part load |  | HR (kJ/kWh) | Eff | Part load |  | HR (kJ/kWh) | Eff | Part load |  | HR (kJ/kWh) | Eff | Part load |  | HR (kJ/kWh) | Eff |  |  |  |  | T in -20 C |  | 0 |  |  |  | T in -15 C |  | 0 |  |  |  | T in -10 C |  | 0 |  |  |  | T in -5 C |  | 0 |  |  |  | T in 0 C |  | 0 |  |  |  | T in 5 C |  | 0 |  |  |  | T in 10 C |  | 0 |  |  |  | T in 15 C |  | 0 |  |  |  | T in 20 C |  | 0 |  |  |  | T in 25 C |  | 0
0.081281 |  | 0 | #DIV/0! | 0.080071 |  | 0 | #DIV/0! | 0.075725 | 3.9797 | 33693.0833 | 10.68% | 0.076398 | 3.9306 | 33310.5105 | 10.81% | 0.077963 | 3.8678 | 32881.4986 | 10.95% | 0.081136 | 3.8463 | 32927.3866 | 10.93% | 0.084595 | 3.8144 | 32919.5037 | 10.94% | 0.090166 | 3.7604 | 32890.1987 | 10.95% | 0.096674 | 3.6963 | 32849.2134 | 10.96% | 0.10397 | 3.6332 | 32806.459 | 10.97% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.095568 |  | 0 | #DIV/0! | 0.094145 |  | 0 | #DIV/0! | 0.085696 | 3.587 | 30368.4872 | 11.85% | 0.086458 | 3.5432 | 30027.3093 | 11.99% | 0.088229 | 3.5341 | 30044.2987 | 11.98% | 0.09182 | 3.507 | 30023.1877 | 11.99% | 0.095734 | 3.4779 | 30015.2005 | 11.99% | 0.10204 | 3.429 | 29991.3969 | 12% | 0.1094 | 3.371 | 29958.4076 | 12.02% | 0.11766 | 3.3143 | 29926.432 | 12.03% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.10983 |  | 0 | #DIV/0! | 0.10819 |  | 0 | #DIV/0! | 0.095647 | 3.2749 | 27726.4862 | 12.98% | 0.096497 | 3.2804 | 27800.8102 | 12.95% | 0.098475 | 3.2643 | 27750.7988 | 12.97% | 0.10248 | 3.2399 | 27736.4949 | 12.98% | 0.10685 | 3.2135 | 27733.703 | 12.98% | 0.11389 | 3.1677 | 27706.1987 | 12.99% | 0.12211 | 3.1141 | 27675.7106 | 13.01% | 0.13132 | 3.052 | 27558.4014 | 13.06% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.12411 |  | 0 | #DIV/0! | 0.12226 |  | 0 | #DIV/0! | 0.1056 | 3.0631 | 25932.8928 | 13.88% | 0.10654 | 3.0594 | 25927.9096 | 13.88% | 0.10872 | 3.0448 | 25884.7989 | 13.91% | 0.11314 | 3.0223 | 25873.7892 | 13.91% | 0.11797 | 2.9977 | 25870.9994 | 13.92% | 0.12574 | 2.9555 | 25849.8015 | 13.93% | 0.13481 | 2.8918 | 25700.1076 | 14.01% | 0.14498 | 2.8157 | 25424.2827 | 14.16% |  | Correction factors |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.13837 |  | 0 | #DIV/0! | 0.13631 |  | 0 | #DIV/0! | 0.11557 | 2.8792 | 24376.288 | 14.77% | 0.1166 | 2.8759 | 24372.5052 | 14.77% | 0.11899 | 2.8624 | 24334.2989 | 14.79% | 0.12383 | 2.8417 | 24327.6911 | 14.8% | 0.12911 | 2.8183 | 24323.1982 | 14.8% | 0.13761 | 2.7651 | 24184.3033 | 14.89% | 0.14754 | 2.6907 | 23912.7067 | 15.05% | 0.15867 | 2.6187 | 23645.4605 | 15.22% |  |  | 1.0216 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.15263 |  | 0 | #DIV/0! | 0.15035 |  | 0 | #DIV/0! | 0.12552 | 2.7248 | 23069.2865 | 15.61% | 0.12664 | 2.7215 | 23063.6044 | 15.61% | 0.12923 | 2.7087 | 23027.399 | 15.63% | 0.13449 | 2.6889 | 23019.0894 | 15.64% | 0.14022 | 2.657 | 22930.3022 | 15.7% | 0.14946 | 2.5904 | 22656.9982 | 15.89% | 0.16025 | 2.52 | 22395.3049 | 16.07% | 0.17233 | 2.4513 | 22134.646 | 16.26% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.16689 |  | 0 | #DIV/0! | 0.1644 |  | 0 | #DIV/0! | 0.13547 | 2.5921 | 21945.3941 | 16.4% | 0.13668 | 2.5895 | 21945.5031 | 16.4% | 0.13948 | 2.5781 | 21917.5991 | 16.43% | 0.14515 | 2.5509 | 21837.891 | 16.49% | 0.15134 | 2.5043 | 21612.9042 | 16.66% | 0.16131 | 2.4403 | 21343.9011 | 16.87% | 0.17295 | 2.3727 | 21086.0035 | 17.07% | 0.186 | 2.3062 | 20824.0267 | 17.29% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.18114 |  | 0 | #DIV/0! | 0.17845 |  | 0 | #DIV/0! | 0.14542 | 2.4776 | 20976.4942 | 17.16% | 0.14672 | 2.4752 | 20976.8023 | 17.16% | 0.14972 | 2.4586 | 20901.0991 | 17.22% | 0.15582 | 2.4157 | 20680.1922 | 17.41% | 0.16246 | 2.3696 | 20450.7048 | 17.6% | 0.17316 | 2.3092 | 20197.0032 | 17.82% | 0.18565 | 2.2445 | 19947.4056 | 18.05% | 0.19966 | 2.1788 | 19673.8182 | 18.3% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.1954 |  | 0 | #DIV/0! | 0.19249 |  | 0 | #DIV/0! | 0.15539 | 2.3776 | 20129.7884 | 17.88% | 0.15677 | 2.3715 | 20097.4079 | 17.91% | 0.15999 | 2.338 | 19876.2991 | 18.11% | 0.1665 | 2.2972 | 19666.094 | 18.31% | 0.1736 | 2.2517 | 19432.5969 | 18.53% | 0.18503 | 2.1938 | 19188.2022 | 18.76% | 0.19838 | 2.1306 | 18935.1112 | 19.01% | 0.21335 | 2.2271 | 20110.2188 | 17.9% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.20966 |  | 0 | #DIV/0! | 0.20654 |  | 0 | #DIV/0! | 0.16534 | 2.2887 | 19376.796 | 18.58% | 0.16681 | 2.2632 | 19179.6062 | 18.77% | 0.17023 | 2.2312 | 18968.4992 | 18.98% | 0.17716 | 2.1911 | 18757.4917 | 19.19% | 0.18471 | 2.1477 | 18535.0025 | 19.42% | 0.19688 | 2.0919 | 18296.8041 | 19.68% | 0.21109 | 2.1799 | 19372.9077 | 18.58% | 0.22701 | 2.1472 | 19387.914 | 18.57% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.22392 |  | 0 | #DIV/0! | 0.22058 |  | 0 | #DIV/0! | 0.1753 | 2.1912 | 18551.4929 | 19.41% | 0.17685 | 2.1667 | 18362.3059 | 19.61% | 0.18048 | 2.1362 | 18160.2992 | 19.82% | 0.18782 | 2.0965 | 17947.5965 | 20.06% | 0.19583 | 2.0544 | 17729.8041 | 20.3% | 0.20873 | 2.1396 | 18714.1036 | 19.24% | 0.22379 | 2.1073 | 18727.9084 | 19.22% | 0.24067 | 2.076 | 18745.8101 | 19.2% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.23815 |  | 0 | #DIV/0! | 0.2346 |  | 0 | #DIV/0! | 0.18525 | 2.104 | 17813.3927 | 20.21% | 0.18689 | 2.0804 | 17630.507 | 20.42% | 0.19072 | 2.0509 | 17435.1992 | 20.65% | 0.19848 | 2.0117 | 17221.992 | 20.9% | 0.20695 | 2.1003 | 18126.0039 | 19.86% | 0.22057 | 2.0734 | 18134.8033 | 19.85% | 0.2365 | 2.0418 | 18146.0075 | 19.84% | 0.25434 | 2.0115 | 18163.0036 | 19.82% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.2524 |  | 0 | #DIV/0! | 0.24865 |  | 0 | #DIV/0! | 0.1952 | 2.0257 | 17150.2954 | 20.99% | 0.19693 | 2.0027 | 16972.1074 | 21.21% | 0.20097 | 1.9729 | 16772.1993 | 21.46% | 0.20915 | 1.9345 | 16561.2961 | 21.74% | 0.21806 | 2.0386 | 17593.6007 | 20.46% | 0.23242 | 2.0124 | 17601.5003 | 20.45% | 0.2492 | 1.9823 | 17616.505 | 20.44% | 0.268 | 1.953 | 17634.9978 | 20.41% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.26663 |  | 0 | #DIV/0! | 0.26266 |  | 0 | #DIV/0! | 0.20515 | 1.9546 | 16548.3925 | 21.75% | 0.20697 | 1.9323 | 16376.0053 | 21.98% | 0.21121 | 1.9022 | 16170.7993 | 22.26% | 0.21981 | 1.9962 | 17088.9984 | 21.07% | 0.22918 | 1.9822 | 17107.1021 | 21.04% | 0.24427 | 1.9571 | 17117.5007 | 21.03% | 0.2619 | 1.9281 | 17135.3039 | 21.01% | 0.28166 | 1.8997 | 17153.8917 | 20.99% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.28086 |  | 0 | #DIV/0! | 0.27668 |  | 0 | #DIV/0! | 0.2151 | 1.89 | 16001.292 | 22.5% | 0.21701 | 1.8674 | 15825.404 | 22.75% | 0.22146 | 1.9551 | 16621.0993 | 21.66% | 0.23047 | 1.9436 | 16639.0976 | 21.64% | 0.2403 | 1.9305 | 16660.3977 | 21.61% | 0.25612 | 1.9065 | 16675.0991 | 21.59% | 0.27461 | 1.8786 | 16695.6056 | 21.56% | 0.29532 | 1.8481 | 16687.7838 | 21.57% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.29509 |  | 0 | #DIV/0! | 0.2907 |  | 0 | #DIV/0! | 0.22505 | 1.8307 | 15499.2914 | 23.23% | 0.22705 | 1.8073 | 15315.9049 | 23.5% | 0.2317 | 1.9069 | 16211.1993 | 22.21% | 0.24113 | 1.8956 | 16228.0974 | 22.18% | 0.25141 | 1.8827 | 16248.3009 | 22.16% | 0.26797 | 1.8598 | 16266.7034 | 22.13% | 0.28731 | 1.8296 | 16260.102 | 22.14% | 0.30899 | 1.8034 | 16284.278 | 22.11% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.30932 |  | 0 | #DIV/0! | 0.30472 |  | 0 | #DIV/0! | 0.235 | 1.7757 | 15033.6959 | 23.95% | 0.23709 | 1.8697 | 15845.5059 | 22.72% | 0.24195 | 1.8638 | 15845.0993 | 22.72% | 0.2518 | 1.8524 | 15858.1982 | 22.7% | 0.26253 | 1.8396 | 15876.3004 | 22.68% | 0.27982 | 1.8172 | 15893.8969 | 22.65% | 0.30002 | 1.7873 | 15884.1064 | 22.66% | 0.32265 | 1.7602 | 15893.477 | 22.65% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.32355 |  | 0 | #DIV/0! | 0.31873 |  | 0 | #DIV/0! | 0.24495 | 1.8321 | 15510.7971 | 23.21% | 0.24713 | 1.8312 | 15519.0011 | 23.2% | 0.2522 | 1.8253 | 15517.1993 | 23.2% | 0.26246 | 1.8138 | 15527.893 | 23.18% | 0.27365 | 1.8011 | 15544.3963 | 23.16% | 0.29167 | 1.7754 | 15528.4985 | 23.18% | 0.31272 | 1.7475 | 15530.1064 | 23.18% | 0.33631 | 1.7206 | 15536.1757 | 23.17% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.33778 |  | 0 | #DIV/0! | 0.33275 |  | 0 | #DIV/0! | 0.2549 | 1.7952 | 15198.7971 | 23.69% | 0.25717 | 1.7953 | 15214.9034 | 23.66% | 0.26244 | 1.7901 | 15218.1993 | 23.66% | 0.27312 | 1.7789 | 15229.3917 | 23.64% | 0.28476 | 1.766 | 15240.9032 | 23.62% | 0.30352 | 1.7399 | 15218.0013 | 23.66% | 0.32543 | 1.7117 | 15211.8059 | 23.67% | 0.34997 | 1.6747 | 15121.8706 | 23.81% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.35201 |  | 0 | #DIV/0! | 0.34677 |  | 0 | #DIV/0! | 0.26486 | 1.7607 | 14906.3967 | 24.15% | 0.26721 | 1.7613 | 14926.7042 | 24.12% | 0.27269 | 1.7562 | 14930.1994 | 24.11% | 0.28378 | 1.746 | 14947.1988 | 24.08% | 0.29588 | 1.7304 | 14934.1046 | 24.11% | 0.31537 | 1.7074 | 14933.2972 | 24.11% | 0.33813 | 1.6704 | 14845.0085 | 24.25% | 0.36364 | 1.6435 | 14840.1651 | 24.26% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.36621 |  | 0 | #DIV/0! | 0.36076 |  | 0 | #DIV/0! | 0.27481 | 1.7286 | 14634.5947 | 24.6% | 0.27725 | 1.7291 | 14653.9035 | 24.57% | 0.28293 | 1.7245 | 14660.7994 | 24.56% | 0.29445 | 1.7139 | 14672.8991 | 24.54% | 0.307 | 1.6986 | 14659.2037 | 24.56% | 0.32721 | 1.6772 | 14669.1035 | 24.54% | 0.35084 | 1.641 | 14584.0032 | 24.68% | 0.3773 | 1.6148 | 14581.1601 | 24.69% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.38041 |  | 0 | #DIV/0! | 0.37475 |  | 0 | #DIV/0! | 0.28474 | 1.6987 | 14381.9943 | 25.03% | 0.28727 | 1.6986 | 14394.7048 | 25.01% | 0.29316 | 1.6939 | 14400.5994 | 25% | 0.30509 | 1.6811 | 14391.7934 | 25.01% | 0.31809 | 1.6693 | 14406.8019 | 24.99% | 0.33904 | 1.6386 | 14332.2009 | 25.12% | 0.36351 | 1.6127 | 14332.0094 | 25.12% | 0.39093 | 1.5874 | 14333.8574 | 25.12% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.39464 |  | 0 | #DIV/0! | 0.38876 |  | 0 | #DIV/0! | 0.29469 | 1.6716 | 14152.2952 | 25.44% | 0.29731 | 1.6702 | 14154.0995 | 25.43% | 0.3034 | 1.6649 | 14154.1994 | 25.43% | 0.31575 | 1.6524 | 14145.7961 | 25.45% | 0.32921 | 1.6314 | 14079.6013 | 25.57% | 0.35089 | 1.611 | 14090.5991 | 25.55% | 0.37622 | 1.5863 | 14097.2032 | 25.54% | 0.4046 | 1.5614 | 14098.8531 | 25.53% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.40884 |  | 0 | #DIV/0! | 0.40275 |  | 0 | #DIV/0! | 0.30464 | 1.6456 | 13931.8921 | 25.84% | 0.30735 | 1.6444 | 13935.6048 | 25.83% | 0.31365 | 1.6371 | 13917.0994 | 25.87% | 0.32641 | 1.6262 | 13922.0998 | 25.86% | 0.34033 | 1.6053 | 13854.4972 | 25.98% | 0.36274 | 1.5848 | 13861.6971 | 25.97% | 0.38892 | 1.5607 | 13869.9067 | 25.96% | 0.41826 | 1.5368 | 13876.2554 | 25.94% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.42304 |  | 0 | #DIV/0! | 0.41674 |  | 0 | #DIV/0! | 0.31459 | 1.6209 | 13723.0963 | 26.23% | 0.31739 | 1.6198 | 13727.6017 | 26.22% | 0.32389 | 1.6127 | 13709.8994 | 26.26% | 0.33707 | 1.5941 | 13647.1923 | 26.38% | 0.35144 | 1.5816 | 13649.3981 | 26.37% | 0.37459 | 1.5612 | 13654.8972 | 26.36% | 0.40163 | 1.5369 | 13658.7047 | 26.36% | 0.43192 | 1.5134 | 13665.8476 | 26.34% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.43724 |  | 0 | #DIV/0! | 0.43073 |  | 0 | #DIV/0! | 0.32452 | 1.5976 | 13526.094 | 26.62% | 0.32741 | 1.5951 | 13517.6071 | 26.63% | 0.33412 | 1.5905 | 13520.9994 | 26.63% | 0.34771 | 1.5719 | 13457.2944 | 26.75% | 0.36254 | 1.5605 | 13467.4973 | 26.73% | 0.38641 | 1.5402 | 13471.0041 | 26.72% | 0.4143 | 1.5166 | 13478.4031 | 26.71% | 0.44556 | 1.4925 | 13476.6504 | 26.71% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.45141 |  | 0 | #DIV/0! | 0.44469 |  | 0 | #DIV/0! | 0.33448 | 1.573 | 13317.5945 | 27.03% | 0.33745 | 1.5735 | 13335.2993 | 27% | 0.34436 | 1.5606 | 13267.2994 | 27.13% | 0.35838 | 1.5506 | 13274.7932 | 27.12% | 0.37366 | 1.5393 | 13284.5004 | 27.1% | 0.39826 | 1.5201 | 13295.4026 | 27.08% | 0.42701 | 1.497 | 13303.7093 | 27.06% | 0.45922 | 1.4662 | 13238.9462 | 27.19% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.46562 |  | 0 | #DIV/0! | 0.45868 |  | 0 | #DIV/0! | 0.34441 | 1.5535 | 13152.7981 | 27.37% | 0.34747 | 1.5535 | 13165.1018 | 27.35% | 0.35459 | 1.5407 | 13097.6994 | 27.49% | 0.36902 | 1.5308 | 13104.7995 | 27.47% | 0.38475 | 1.5201 | 13118.7986 | 27.44% | 0.41008 | 1.5014 | 13131.8974 | 27.41% | 0.43969 | 1.475 | 13108.1042 | 27.46% | 0.47285 | 1.4376 | 12980.8442 | 27.73% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.47979 |  | 0 | #DIV/0! | 0.47264 |  | 0 | #DIV/0! | 0.35436 | 1.5343 | 12989.7964 | 27.71% | 0.35751 | 1.526 | 12932.5052 | 27.84% | 0.36483 | 1.5214 | 12934.0994 | 27.83% | 0.37968 | 1.5123 | 12946.9964 | 27.81% | 0.39587 | 1.5024 | 12965.9992 | 27.76% | 0.42193 | 1.4835 | 12975.1007 | 27.75% | 0.45239 | 1.4468 | 12857.7011 | 28% | 0.48652 | 1.4114 | 12744.4402 | 28.25% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.49399 |  | 0 | #DIV/0! | 0.48663 |  | 0 | #DIV/0! | 0.36429 | 1.5083 | 12770.0961 | 28.19% | 0.36753 | 1.5081 | 12780.6046 | 28.17% | 0.37506 | 1.5037 | 12783.0994 | 28.16% | 0.39032 | 1.4954 | 12802.3001 | 28.12% | 0.40696 | 1.4855 | 12820.1039 | 28.08% | 0.43376 | 1.4578 | 12750.0996 | 28.24% | 0.46507 | 1.4207 | 12625.6055 | 28.51% | 0.50015 | 1.3865 | 12519.7386 | 28.75% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.50816 |  | 0 | #DIV/0! | 0.50059 |  | 0 | #DIV/0! | 0.37424 | 1.4912 | 12624.5943 | 28.52% | 0.37756 | 1.4912 | 12637.6025 | 28.49% | 0.3853 | 1.4877 | 12647.3995 | 28.46% | 0.40098 | 1.4793 | 12664.3927 | 28.43% | 0.41808 | 1.4662 | 12653.7981 | 28.45% | 0.44561 | 1.4316 | 12520.9964 | 28.75% | 0.47777 | 1.3961 | 12407.1072 | 29.02% | 0.51381 | 1.3624 | 12302.1343 | 29.26% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.52233 |  | 0 | #DIV/0! | 0.51455 |  | 0 | #DIV/0! | 0.38417 | 1.4755 | 12492.2915 | 28.82% | 0.38759 | 1.4756 | 12505.4988 | 28.79% | 0.39553 | 1.4722 | 12515.1995 | 28.77% | 0.41162 | 1.4639 | 12532.4949 | 28.73% | 0.42917 | 1.4417 | 12442.2004 | 28.93% | 0.45743 | 1.4076 | 12311.3977 | 29.24% | 0.49045 | 1.3728 | 12200.1088 | 29.51% | 0.52745 | 1.3395 | 12094.7334 | 29.77% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.5365 |  | 0 | #DIV/0! | 0.52851 |  | 0 | #DIV/0! | 0.39412 | 1.4604 | 12364.1964 | 29.12% | 0.39762 | 1.461 | 12381.2004 | 29.08% | 0.40577 | 1.4576 | 12391.0995 | 29.05% | 0.42229 | 1.4438 | 12360.1983 | 29.13% | 0.44029 | 1.4188 | 12244.7995 | 29.4% | 0.46928 | 1.3849 | 12112.4958 | 29.72% | 0.50316 | 1.3503 | 12000.4067 | 30% | 0.54111 | 1.3172 | 11893.7345 | 30.27% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.55068 |  | 0 | #DIV/0! | 0.54248 |  | 0 | #DIV/0! | 0.40405 | 1.4469 | 12249.495 | 29.39% | 0.40764 | 1.4469 | 12261.902 | 29.36% | 0.416 | 1.4429 | 12266.5995 | 29.35% | 0.43293 | 1.4219 | 12172.6975 | 29.57% | 0.45138 | 1.3963 | 12050.402 | 29.87% | 0.48111 | 1.3628 | 11919.8038 | 30.2% | 0.51584 | 1.3287 | 11808.2053 | 30.49% | 0.55475 | 1.2957 | 11699.3272 | 30.77% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.56485 |  | 0 | #DIV/0! | 0.55644 |  | 0 | #DIV/0! | 0.41398 | 1.4341 | 12141.8969 | 29.65% | 0.41766 | 1.4334 | 12147.2986 | 29.64% | 0.42622 | 1.4241 | 12106.7995 | 29.74% | 0.44357 | 1.4007 | 11991.3948 | 30.02% | 0.46248 | 1.375 | 11866.404 | 30.34% | 0.49293 | 1.3417 | 11734.8962 | 30.68% | 0.52851 | 1.3076 | 11620.9007 | 30.98% | 0.56838 | 1.275 | 11512.6312 | 31.27% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.57902 |  | 0 | #DIV/0! | 0.5704 |  | 0 | #DIV/0! | 0.42391 | 1.4231 | 12048.5983 | 29.88% | 0.42768 | 1.4207 | 12039.7038 | 29.9% | 0.43645 | 1.4034 | 11930.7995 | 30.17% | 0.45421 | 1.3807 | 11820.0998 | 30.46% | 0.47357 | 1.3544 | 11688.9046 | 30.8% | 0.50476 | 1.3211 | 11555.0002 | 31.16% | 0.54119 | 1.2875 | 11441.8078 | 31.46% | 0.58202 | 1.2549 | 11331.5246 | 31.77% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.59316 |  | 0 | #DIV/0! | 0.58433 |  | 0 | #DIV/0! | 0.43387 | 1.4118 | 11952.7937 | 30.12% | 0.43772 | 1.4007 | 11870.7013 | 30.33% | 0.44669 | 1.3833 | 11760.0995 | 30.61% | 0.46487 | 1.3604 | 11645.9968 | 30.91% | 0.48469 | 1.3344 | 11516.4022 | 31.26% | 0.5166 | 1.3013 | 11381.804 | 31.63% | 0.5539 | 1.2679 | 11268.4027 | 31.95% | 0.59568 | 1.2357 | 11157.6235 | 32.26% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.60733 |  | 0 | #DIV/0! | 0.59829 |  | 0 | #DIV/0! | 0.4438 | 1.3934 | 11796.5989 | 30.52% | 0.44774 | 1.3807 | 11701.1988 | 30.77% | 0.45692 | 1.3639 | 11594.8995 | 31.05% | 0.47551 | 1.3405 | 11475.6007 | 31.37% | 0.49578 | 1.315 | 11348.8967 | 31.72% | 0.52843 | 1.2822 | 11214.3979 | 32.1% | 0.56658 | 1.2489 | 11099.2011 | 32.43% | 0.60931 | 1.217 | 10989.2215 | 32.76% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.62148 |  | 0 | #DIV/0! | 0.61222 |  | 0 | #DIV/0! | 0.45373 | 1.3751 | 11641.9959 | 30.92% | 0.45776 | 1.3625 | 11546.8999 | 31.18% | 0.46714 | 1.3459 | 11441.7995 | 31.46% | 0.48615 | 1.3221 | 11318.2942 | 31.81% | 0.50688 | 1.297 | 11193.301 | 32.16% | 0.54026 | 1.264 | 11055.7032 | 32.56% | 0.57925 | 1.2309 | 10939.3044 | 32.91% | 0.62295 | 1.1993 | 10829.524 | 33.24% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.63562 |  | 0 | #DIV/0! | 0.62616 |  | 0 | #DIV/0! | 0.46366 | 1.3572 | 11490.2968 | 31.33% | 0.46778 | 1.345 | 11398.1011 | 31.58% | 0.47737 | 1.3281 | 11290.4995 | 31.89% | 0.49679 | 1.3048 | 11169.8996 | 32.23% | 0.51797 | 1.2798 | 11044.9979 | 32.59% | 0.55208 | 1.2471 | 10907.6967 | 33% | 0.59193 | 1.2142 | 10791.103 | 33.36% | 0.63658 | 1.1826 | 10678.8199 | 33.71% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.64977 |  | 0 | #DIV/0! | 0.64009 |  | 0 | #DIV/0! | 0.47359 | 1.3401 | 11345.5993 | 31.73% | 0.4778 | 1.3277 | 11251.904 | 31.99% | 0.48759 | 1.3106 | 11141.9995 | 32.31% | 0.50743 | 1.2881 | 11027.3008 | 32.65% | 0.52907 | 1.2631 | 10900.8978 | 33.02% | 0.5639 | 1.2304 | 10761.3956 | 33.45% | 0.60461 | 1.1977 | 10644.2081 | 33.82% | 0.65022 | 1.1689 | 10554.5185 | 34.11% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.66391 |  | 0 | #DIV/0! | 0.65402 |  | 0 | #DIV/0! | 0.48352 | 1.3236 | 11206.0917 | 32.13% | 0.48782 | 1.3114 | 11113.9019 | 32.39% | 0.49781 | 1.2943 | 11003.4995 | 32.72% | 0.51807 | 1.2719 | 10888.1947 | 33.06% | 0.54016 | 1.2468 | 10760.3015 | 33.46% | 0.57573 | 1.2142 | 10619.5028 | 33.9% | 0.61729 | 1.1825 | 10509.2041 | 34.26% | 0.66385 | 1.1579 | 10455.8159 | 34.43% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.67805 |  | 0 | #DIV/0! | 0.66795 |  | 0 | #DIV/0! | 0.49345 | 1.308 | 11073.9921 | 32.51% | 0.49784 | 1.2956 | 10980.1034 | 32.79% | 0.50804 | 1.2786 | 10870.0995 | 33.12% | 0.52872 | 1.2563 | 10754.9957 | 33.47% | 0.55126 | 1.231 | 10624.2966 | 33.88% | 0.58756 | 1.1986 | 10483.6974 | 34.34% | 0.62997 | 1.1718 | 10414.3076 | 34.57% | 0.67749 | 1.1474 | 10360.2105 | 34.75% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.69217 |  | 0 | #DIV/0! | 0.68186 |  | 0 | #DIV/0! | 0.50338 | 1.2929 | 10946.3965 | 32.89% | 0.50786 | 1.2802 | 10849.7031 | 33.18% | 0.51826 | 1.2633 | 10739.3995 | 33.52% | 0.53936 | 1.241 | 10624.3992 | 33.88% | 0.56235 | 1.2155 | 10489.802 | 34.32% | 0.59938 | 1.1863 | 10375.4957 | 34.7% | 0.64265 | 1.1612 | 10320.0066 | 34.88% | 0.69112 | 1.1369 | 10266.1131 | 35.07% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.70631 |  | 0 | #DIV/0! | 0.69579 |  | 0 | #DIV/0! | 0.51329 | 1.2786 | 10824.7951 | 33.26% | 0.51786 | 1.2654 | 10724.0063 | 33.57% | 0.52847 | 1.2486 | 10614.4995 | 33.92% | 0.54997 | 1.2262 | 10496.996 | 34.3% | 0.57342 | 1.2006 | 10361.2019 | 34.75% | 0.61118 | 1.176 | 10285.6964 | 35% | 0.6553 | 1.1511 | 10229.8025 | 35.19% | 0.70473 | 1.127 | 10175.9164 | 35.38% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.72042 |  | 0 | #DIV/0! | 0.7097 |  | 0 | #DIV/0! | 0.52323 | 1.2642 | 10703.2953 | 33.63% | 0.52788 | 1.251 | 10602.1995 | 33.96% | 0.53869 | 1.2342 | 10492.3995 | 34.31% | 0.56062 | 1.2118 | 10373.993 | 34.7% | 0.58452 | 1.1885 | 10256.9997 | 35.1% | 0.62301 | 1.1661 | 10198.8972 | 35.3% | 0.66798 | 1.1414 | 10143.8997 | 35.49% | 0.71837 | 1.1173 | 10088.7085 | 35.68% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.73457 |  | 0 | #DIV/0! | 0.72363 |  | 0 | #DIV/0! | 0.53316 | 1.2503 | 10584.9957 | 34.01% | 0.5379 | 1.2371 | 10484.2062 | 34.34% | 0.54892 | 1.2204 | 10375.0996 | 34.7% | 0.57126 | 1.1979 | 10255.3989 | 35.1% | 0.59561 | 1.1789 | 10174.3042 | 35.38% | 0.63483 | 1.1566 | 10116.1037 | 35.59% | 0.68066 | 1.132 | 10060.6009 | 35.78% | 0.732 | 1.1083 | 10007.5144 | 35.97% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.74868 |  | 0 | #DIV/0! | 0.73753 |  | 0 | #DIV/0! | 0.54307 | 1.2365 | 10468.5926 | 34.39% | 0.5479 | 1.2234 | 10368.2045 | 34.72% | 0.55912 | 1.2069 | 10260.2996 | 35.09% | 0.58188 | 1.1859 | 10152.0945 | 35.46% | 0.60668 | 1.1697 | 10094.6033 | 35.66% | 0.64663 | 1.1475 | 10036.3978 | 35.87% | 0.69331 | 1.123 | 9980.5014 | 36.07% | 0.74561 | 1.0994 | 9927.3135 | 36.26% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.553 | 1.2232 | 10355.9993 | 34.76% | 0.55792 | 1.2103 | 10256.6011 | 35.1% | 0.56935 | 1.1938 | 10148.8996 | 35.47% | 0.59252 | 1.1767 | 10073.8993 | 35.74% | 0.61778 | 1.1606 | 10016.4991 | 35.94% | 0.65846 | 1.1386 | 9958.8959 | 36.15% | 0.70599 | 1.1143 | 9902.8015 | 36.35% | 0.75924 | 1.0908 | 9849.8124 | 36.55% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.56293 | 1.2102 | 10245.4972 | 35.14% | 0.56793 | 1.1974 | 10147.8029 | 35.48% | 0.57957 | 1.1832 | 10058.4996 | 35.79% | 0.60316 | 1.1679 | 9998.4007 | 36.01% | 0.62887 | 1.1519 | 9941.3982 | 36.21% | 0.67028 | 1.1301 | 9884.0005 | 36.42% | 0.71867 | 1.1059 | 9828.4075 | 36.63% | 0.77288 | 1.0824 | 9773.5123 | 36.83% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.57284 | 1.1974 | 10137.3995 | 35.51% | 0.57793 | 1.186 | 10050.9031 | 35.82% | 0.58978 | 1.1745 | 9985.0996 | 36.05% | 0.61378 | 1.1593 | 9924.7941 | 36.27% | 0.63994 | 1.1435 | 9868.8002 | 36.48% | 0.68208 | 1.1218 | 9812.0002 | 36.69% | 0.73132 | 1.0977 | 9755.4 | 36.9% | 0.78649 | 1.0742 | 9699.903 | 37.11% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.58277 | 1.1859 | 10040.0964 | 35.86% | 0.58795 | 1.1775 | 9978.6055 | 36.08% | 0.6 | 1.1662 | 9914.0996 | 36.31% | 0.62442 | 1.1511 | 9854.5006 | 36.53% | 0.65104 | 1.1354 | 9798.6962 | 36.74% | 0.69391 | 1.1137 | 9740.9007 | 36.96% | 0.744 | 1.0898 | 9685.3074 | 37.17% | 0.80012 | 1.0661 | 9626.6097 | 37.4% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.59268 | 1.1778 | 9971.1977 | 36.1% | 0.59795 | 1.1694 | 9910.2994 | 36.33% | 0.6102 | 1.1581 | 9845.6996 | 36.56% | 0.63504 | 1.1431 | 9785.7994 | 36.79% | 0.66211 | 1.1275 | 9730.8017 | 37% | 0.70571 | 1.106 | 9673.0986 | 37.22% | 0.75665 | 1.0821 | 9617.0011 | 37.43% | 0.81373 | 1.0583 | 9556.1066 | 37.67% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.60259 | 1.1698 | 9903.4927 | 36.35% | 0.60795 | 1.1614 | 9842.2051 | 36.58% | 0.62041 | 1.1503 | 9778.9996 | 36.81% | 0.64566 | 1.1354 | 9720.0945 | 37.04% | 0.67318 | 1.1198 | 9664.4001 | 37.25% | 0.71751 | 1.0983 | 9606.3023 | 37.48% | 0.76931 | 1.0746 | 9549.8057 | 37.7% | 0.82734 | 1.0521 | 9499.6084 | 37.9% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.61253 | 1.1621 | 9838.2938 | 36.59% | 0.61797 | 1.1537 | 9777.3991 | 36.82% | 0.63063 | 1.1427 | 9714.1996 | 37.06% | 0.6563 | 1.1278 | 9655.3998 | 37.28% | 0.68428 | 1.1125 | 9601.0019 | 37.5% | 0.72934 | 1.0922 | 9552.8968 | 37.68% | 0.78198 | 1.0696 | 9505.2014 | 37.87% | 0.84097 | 1.0469 | 9453.3046 | 38.08% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.62244 | 1.1546 | 9775.1945 | 36.83% | 0.62797 | 1.1461 | 9712.7032 | 37.06% | 0.64084 | 1.1352 | 9651.0996 | 37.3% | 0.66692 | 1.121 | 9596.9974 | 37.51% | 0.69535 | 1.1078 | 9560.6984 | 37.65% | 0.74114 | 1.0874 | 9510.503 | 37.85% | 0.79464 | 1.0647 | 9462.5077 | 38.04% | 0.85458 | 1.0412 | 9401.4025 | 38.29% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.63235 | 1.1472 | 9712.6963 | 37.06% | 0.63797 | 1.139 | 9652.4989 | 37.3% | 0.65104 | 1.1289 | 9596.8996 | 37.51% | 0.67754 | 1.1164 | 9557.797 | 37.67% | 0.70642 | 1.1032 | 9520.9991 | 37.81% | 0.75294 | 1.0829 | 9471.3016 | 38.01% | 0.80729 | 1.0601 | 9421.2005 | 38.21% | 0.86819 | 1.0356 | 9350.9993 | 38.5% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.64226 | 1.1402 | 9652.9919 | 37.29% | 0.64797 | 1.1319 | 9592.4048 | 37.53% | 0.66125 | 1.1244 | 9558.5996 | 37.66% | 0.68816 | 1.1119 | 9518.8963 | 37.82% | 0.71749 | 1.0987 | 9482.1023 | 37.97% | 0.76474 | 1.0785 | 9433.2023 | 38.16% | 0.81994 | 1.0556 | 9380.7997 | 38.38% | 0.88179 | 1.0298 | 9299.0068 | 38.71% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.65217 | 1.1332 | 9593.694 | 37.52% | 0.65797 | 1.125 | 9533.8023 | 37.76% | 0.67145 | 1.1198 | 9520.0996 | 37.81% | 0.69878 | 1.1075 | 9480.9972 | 37.97% | 0.72857 | 1.0944 | 9445.3027 | 38.11% | 0.77654 | 1.0742 | 9395.103 | 38.32% | 0.8326 | 1.0511 | 9340.8077 | 38.54% | 0.8954 | 1.0239 | 9245.7051 | 38.94% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.8954 | 1.0239 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.66208 | 1.1264 | 9536.0978 | 37.75% | 0.66797 | 1.1195 | 9487.505 | 37.94% | 0.68165 | 1.1157 | 9484.9996 | 37.95% | 0.70939 | 1.1033 | 9445.5979 | 38.11% | 0.73964 | 1.0902 | 9409.0986 | 38.26% | 0.78834 | 1.0699 | 9357.3973 | 38.47% | 0.84525 | 1.0466 | 9301.4023 | 38.7% | 0.90901 | 1.0176 | 9188.7012 | 39.18% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0.90901 | 1.0176
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.67199 | 1.1198 | 9480.5927 | 37.97% | 0.67797 | 1.1146 | 9445.9027 | 38.11% | 0.69186 | 1.1117 | 9450.8996 | 38.09% | 0.72001 | 1.0992 | 9410.3013 | 38.26% | 0.75071 | 1.086 | 9372.299 | 38.41% | 0.80014 | 1.0655 | 9319.0006 | 38.63% | 0.8579 | 1.0422 | 9261.8991 | 38.87% | 0.92262 | 1.0132 | 9149.0974 | 39.35% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.6819 | 1.1135 | 9426.9926 | 38.19% | 0.68797 | 1.1099 | 9406.4021 | 38.27% | 0.70206 | 1.1076 | 9415.6996 | 38.23% | 0.73063 | 1.0949 | 9373.498 | 38.41% | 0.76178 | 1.0817 | 9335.8014 | 38.56% | 0.81194 | 1.0611 | 9280.9013 | 38.79% | 0.87055 | 1.0367 | 9213.0023 | 39.08% | 0.93622 | 1.0111 | 9130.0991 | 39.43% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.69181 | 1.1071 | 9372.7998 | 38.41% | 0.69796 | 1.1057 | 9370.1049 | 38.42% | 0.71227 | 1.1033 | 9379.8996 | 38.38% | 0.74125 | 1.0908 | 9337.7991 | 38.55% | 0.77285 | 1.0777 | 9300.702 | 38.71% | 0.82374 | 1.0568 | 9243.2043 | 38.95% | 0.88321 | 1.0303 | 9156.0004 | 39.32% | 0.94983 | 1.0086 | 9107.498 | 39.53% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.70171 | 1.1017 | 9327.0988 | 38.6% | 0.70794 | 1.1016 | 9335.901 | 38.56% | 0.72245 | 1.0993 | 9345.6996 | 38.52% | 0.75185 | 1.087 | 9305.7984 | 38.69% | 0.7839 | 1.0738 | 9266.8022 | 38.85% | 0.83552 | 1.0526 | 9206.1982 | 39.1% | 0.89584 | 1.0236 | 9096.599 | 39.58% | 0.96341 | 1.0087 | 9107.9044 | 39.53% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.89584 | 1.0236 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.71162 | 1.0976 | 9292.7002 | 38.74% | 0.71794 | 1.0978 | 9303.6039 | 38.69% | 0.73265 | 1.0964 | 9321.0996 | 38.62% | 0.76247 | 1.0835 | 9275.5014 | 38.81% | 0.79498 | 1.0698 | 9232.9024 | 38.99% | 0.84732 | 1.0484 | 9169.4984 | 39.26% | 0.90849 | 1.0179 | 9046.2003 | 39.8% | 0.97702 | 1.0036 | 9061.6999 | 39.73% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0.90849 | 1.0179 | 1 | min | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.72153 | 1.0937 | 9259.3938 | 38.88% | 0.72794 | 1.094 | 9271.0018 | 38.83% | 0.74286 | 1.0934 | 9295.1996 | 38.73% | 0.77309 | 1.0801 | 9246.8994 | 38.93% | 0.80605 | 1.066 | 9200.0986 | 39.13% | 0.85913 | 1.0441 | 9131.6964 | 39.42% | 0.92114 | 1.0155 | 9024.9068 | 39.89% | 0.99063 | 1.0014 | 9042.3043 | 39.81% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.73142 | 1.0899 | 9227.1965 | 39.02% | 0.73792 | 1.0901 | 9238.603 | 38.97% | 0.75304 | 1.0902 | 9268.4996 | 38.84% | 0.78369 | 1.0769 | 9219.1964 | 39.05% | 0.8171 | 1.0623 | 9168.0974 | 39.27% | 0.8709 | 1.0383 | 9081.2034 | 39.64% | 0.93377 | 1.013 | 9002.8045 | 39.99% | 1 | 1 | 9029.5997 | 39.87% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.74133 | 1.0861 | 9195.0923 | 39.15% | 0.74792 | 1.0867 | 9209.6025 | 39.09% | 0.76324 | 1.0872 | 9242.4996 | 38.95% | 0.79431 | 1.0737 | 9191.6988 | 39.17% | 0.82817 | 1.0587 | 9136.5969 | 39.4% | 0.8827 | 1.0312 | 9019.104 | 39.92% | 0.94642 | 1.0111 | 8985.4036 | 40.06% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.75122 | 1.0825 | 9164.9946 | 39.28% | 0.7579 | 1.0838 | 9184.6022 | 39.2% | 0.77343 | 1.0842 | 9216.6996 | 39.06% | 0.8049 | 1.0704 | 9163.2937 | 39.29% | 0.83922 | 1.0542 | 9097.8986 | 39.57% | 0.89448 | 1.024 | 8956.6984 | 40.19% | 0.95905 | 1.0092 | 8968.9002 | 40.14% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.89448 | 1.024 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.76111 | 1.079 | 9134.8969 | 39.41% | 0.76788 | 1.081 | 9161.3984 | 39.3% | 0.78361 | 1.0809 | 9188.9996 | 39.18% | 0.8155 | 1.0661 | 9126.499 | 39.45% | 0.85027 | 1.0492 | 9055.2994 | 39.76% | 0.90626 | 1.0198 | 8919.7974 | 40.36% | 0.97168 | 1.0057 | 8937.5021 | 40.28% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0.90626 | 1.0198 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.77102 | 1.0754 | 9104.6976 | 39.54% | 0.77788 | 1.078 | 9136.1015 | 39.4% | 0.79382 | 1.0765 | 9151.8996 | 39.34% | 0.82612 | 1.0614 | 9086.5966 | 39.62% | 0.86134 | 1.0443 | 9012.5018 | 39.94% | 0.91806 | 1.0172 | 8896.8993 | 40.46% | 0.98433 | 1.0029 | 8912.7071 | 40.39% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.78092 | 1.0721 | 9076.598 | 39.66% | 0.78786 | 1.0751 | 9110.8045 | 39.51% | 0.804 | 1.0719 | 9112.8996 | 39.5% | 0.83672 | 1.0569 | 9047.6959 | 39.79% | 0.87239 | 1.0383 | 8960.7976 | 40.17% | 0.92984 | 1.0145 | 8873.3015 | 40.57% | 0.99696 | 1.0005 | 8891.7069 | 40.49% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.79081 | 1.069 | 9050.0985 | 39.78% | 0.79783 | 1.0721 | 9085.9058 | 39.62% | 0.81418 | 1.0676 | 9076.3996 | 39.66% | 0.84732 | 1.0523 | 9008.7952 | 39.96% | 0.88344 | 1.0315 | 8902.5 | 40.44% | 0.94161 | 1.0121 | 8851.8991 | 40.67% | 1 | 1 | 8887.1033 | 40.51% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.8007 | 1.066 | 9025.1991 | 39.89% | 0.80781 | 1.0692 | 9061.202 | 39.73% | 0.82437 | 1.0635 | 9040.8996 | 39.82% | 0.85791 | 1.0478 | 8970.1941 | 40.13% | 0.89449 | 1.0249 | 8844.9013 | 40.7% | 0.95339 | 1.0106 | 8839.4967 | 40.73% | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.89449 | 1.0249 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.81059 | 1.0631 | 9000.0965 | 40% | 0.81779 | 1.0653 | 9027.8032 | 39.88% | 0.83455 | 1.0591 | 9003.5996 | 39.98% | 0.86851 | 1.0431 | 8930.0007 | 40.31% | 0.90554 | 1.0183 | 8788.0967 | 40.96% | 0.96517 | 1.0066 | 8804.1962 | 40.89% | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0.90554 | 1.0183 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.82048 | 1.0601 | 8975.2988 | 40.11% | 0.82777 | 1.0612 | 8993.201 | 40.03% | 0.84473 | 1.0549 | 8968.1996 | 40.14% | 0.87911 | 1.0385 | 8890.2011 | 40.49% | 0.91659 | 1.0157 | 8766.0981 | 41.07% | 0.97695 | 1.0042 | 8783.5022 | 40.99% | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.83037 | 1.0574 | 8951.8979 | 40.21% | 0.83775 | 1.0572 | 8959.0988 | 40.18% | 0.85492 | 1.0507 | 8932.2996 | 40.3% | 0.88971 | 1.0334 | 8846.7973 | 40.69% | 0.92764 | 1.0136 | 8748.0003 | 41.15% | 0.98872 | 1.0017 | 8761.1989 | 41.09% | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.88971 | 1.0334 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.84026 | 1.0547 | 8929.1998 | 40.32% | 0.84773 | 1.0532 | 8925.4034 | 40.33% | 0.8651 | 1.0463 | 8894.6996 | 40.47% | 0.90031 | 1.0273 | 8794.1992 | 40.94% | 0.93869 | 1.0115 | 8729.9026 | 41.24% | 0.99993 | 0.99997 | 8746.1026 | 41.16% | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0.90031 | 1.0273 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.85013 | 1.0516 | 8903.1998 | 40.43% | 0.85769 | 1.049 | 8890.3012 | 40.49% | 0.87526 | 1.0421 | 8859.0996 | 40.64% | 0.91088 | 1.0208 | 8738.8016 | 41.2% | 0.94972 | 1.0128 | 8740.8976 | 41.19% | 1 | 1 | 8746.4 | 41.16% | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.86002 | 1.0475 | 8868.4964 | 40.59% | 0.86767 | 1.0444 | 8851.3006 | 40.67% | 0.88545 | 1.0377 | 8821.4996 | 40.81% | 0.92148 | 1.0144 | 8684.2944 | 41.45% | 0.96077 | 1.0068 | 8689.297 | 41.43% | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.86991 | 1.0432 | 8831.9982 | 40.76% | 0.87765 | 1.0399 | 8813.1051 | 40.85% | 0.89563 | 1.0331 | 8782.6996 | 40.99% | 0.93208 | 1.0113 | 8657.9011 | 41.58% | 0.97182 | 1.0044 | 8667.9974 | 41.53% | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.89563 | 1.0331 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.87979 | 1.0389 | 8795.5 | 40.93% | 0.8876 | 1.0356 | 8776.1046 | 41.02% | 0.90579 | 1.0289 | 8746.8996 | 41.16% | 0.94266 | 1.0097 | 8644.101 | 41.65% | 0.98284 | 1.0024 | 8650.9008 | 41.61% | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0.90579 | 1.0289 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.88966 | 1.0348 | 8760.9999 | 41.09% | 0.89756 | 1.031 | 8737.5023 | 41.2% | 0.91596 | 1.0236 | 8701.7996 | 41.37% | 0.95323 | 1.0078 | 8628.1006 | 41.72% | 0.99387 | 1.001 | 8638.8011 | 41.67% | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.89756 | 1.031 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.89955 | 1.0308 | 8726.6944 | 41.25% | 0.90754 | 1.0256 | 8691.5017 | 41.42% | 0.92614 | 1.0173 | 8648.1996 | 41.63% | 0.96383 | 1.0092 | 8639.7007 | 41.67% | 1 | 1 | 8630.3003 | 41.71% | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.89955 | 1.0308 | 0 | 0 | 1 | min | 0 | 0 | 0.90754 | 1.0256 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.90942 | 1.0261 | 8686.996 | 41.44% | 0.9175 | 1.0201 | 8645.3061 | 41.64% | 0.9363 | 1.0099 | 8585.6996 | 41.93% | 0.97441 | 1.0035 | 8591.1946 | 41.9% | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0.90942 | 1.0261 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.91929 | 1.021 | 8644.0972 | 41.65% | 0.92746 | 1.0147 | 8599.102 | 41.86% | 0.94646 | 1.0077 | 8567.0996 | 42.02% | 0.98498 | 1.0018 | 8576.4014 | 41.98% | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.92916 | 1.0159 | 8601.0969 | 41.86% | 0.93742 | 1.0093 | 8553.8979 | 42.09% | 0.95663 | 1.0063 | 8554.5996 | 42.08% | 0.99556 | 1.0004 | 8563.9966 | 42.04% | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.93903 | 1.0108 | 8557.995 | 42.07% | 0.94738 | 1.0069 | 8533.2027 | 42.19% | 0.96679 | 1.0048 | 8542.3996 | 42.14% | 1 | 1 | 8560.8976 | 42.05% | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.9489 | 1.006 | 8517.0943 | 42.27% | 0.95734 | 1.0056 | 8522.1008 | 42.24% | 0.97695 | 1.0022 | 8520.2996 | 42.25% | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.95877 | 1.0049 | 8507.4935 | 42.32% | 0.9673 | 1.0044 | 8511.7024 | 42.29% | 0.98712 | 1.0012 | 8511.5996 | 42.3% | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.96864 | 1.0086 | 8539.3945 | 42.16% | 0.97725 | 1.0024 | 8494.8038 | 42.38% | 0.99728 | 1.0004 | 8504.7996 | 42.33% | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.97852 | 1.0031 | 8492.796 | 42.39% | 0.98721 | 1.0015 | 8486.9986 | 42.42% | 0.99998 | 1 | 8501.6996 | 42.34% | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.98839 | 1.0006 | 8471.5964 | 42.49% | 0.99717 | 1.0003 | 8476.9985 | 42.47% | 1 | 1 | 8501.2996 | 42.35% | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.7628 |  | 0 | #DIV/0! | 0.75144 |  | 0 | #DIV/0! | 0.99824 | 0.99996 | 8466.0002 | 42.52% | 1 | 1 | 8474.7018 | 42.48% | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 1 | 1 | 8466.2965 | 42.52% | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[46 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0.89955 | 1.0308 | 0.90942 | 1.0261 |  |  | 0.89756 | 1.031 | 0.90754 | 1.0256 |  |  | 0.89563 | 1.0331 | 0.90579 | 1.0289 |  |  | 0.88971 | 1.0334 | 0.90031 | 1.0273 |  |  | 0.89449 | 1.0249 | 0.90554 | 1.0183 |  |  | 0.89448 | 1.024 | 0.90626 | 1.0198 |  |  | 0.89584 | 1.0236 | 0.90849 | 1.0179 |  |  | 0.8954 | 1.0239 | 0.90901 | 1.0176
[46 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0.89449 | 1.0249 | 0.90554 | 1.0183 |  |  | 0.89448 | 1.024 | 0.90626 | 1.0198 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[48 empty] | -20 | #DIV/0! |  |  |  |  | -15 | #DIV/0! |  |  |  |  | -10 | #DIV/0! |  |  |  |  | -5 | #DIV/0! |  |  |  |  | 0 | #DIV/0! |  |  |  |  | 5 | #DIV/0! |  |  |  |  | 10 | 1.0216 |  |  |  |  | 15 | 1.0221 |  |  |  |  | 20 | #DIV/0! |  |  |  |  | 25 | #DIV/0!
[43 empty] | -20 and -15 | 0 | 0 | 0 | 0 | 0
[43 empty] | -15 and -10 | 0 | 0 | 0 | 0 | 0
[43 empty] | -10 and -5 | 0 | 0 | 0 | 0 | 0
[43 empty] | -5 and 0 | 0 | 0 | 0 | 0 | 0
[43 empty] | 0 and 5 | 0 | 0 | 0 | 0 | 0
[43 empty] | 5 and 10 | 0 | 0 | 0 | 0 | 0
[43 empty] | 10 and 15 | 10 | 15 | 25 | 1.0216 | 1.0221
[43 empty] | 15 and 20 | 0 | 0 | 0 | 0 | 0
[43 empty] | 20 and 25 | 0 | 0 | 0 | 0 | 0
[44 empty] | 10 | 15 |  | 1.0216 | 1.0221

## Part-load_mout_Tin
Inlet Temp | -20 | C | Inlet Temp | -15 | C | Inlet Temp | -10 | C | Inlet Temp | -5 | C | Inlet Temp | 0 | C | Inlet Temp | 5 | C | Inlet Temp | 10 | C | Inlet Temp | 15 | C | Inlet Temp | 20 | C | Inlet Temp | 25 | C
Exhaust flow | 138.525 | kg/s | Exhaust flow | 138.2781 | kg/s | Exhaust flow | 137.533 | kg/s | Exhaust flow | 137.503 | kg/s | Exhaust flow | 136.499 | kg/s | Exhaust flow | 132.911 | kg/s | Exhaust flow | 129.241 | kg/s | Exhaust flow | 122.971 | kg/s | Exhaust flow | 116.851 | kg/s | Exhaust flow | 110.63 | kg/s | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | X | 0 | 0
[30 empty] | T in | 10 | C |  | low | -20 | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20
[30 empty] | Part load | 0.9 |  |  | high | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25
Part load |  | Exh flow (kg/s) | Part load |  | Exh flow (kg/s) | Part load |  | Exh flow (kg/s) | Part load |  | Exh flow (kg/s) | Part load |  | Exh flow (kg/s) | Part load |  | Exh flow (kg/s) | Part load |  | Exh flow (kg/s) | Part load |  | Exh flow (kg/s) | Part load |  | Exh flow (kg/s) | Part load |  | Exh flow (kg/s) |  |  |  |  | T in -20 C |  | 0 |  |  |  | T in -15 C |  | 0 |  |  |  | T in -10 C |  | 0 |  |  |  | T in -5 C |  | 0 |  |  |  | T in 0 C |  | 0 |  |  |  | T in 5 C |  | 0 |  |  |  | T in 10 C |  | 0 |  |  |  | T in 15 C |  | 0 |  |  |  | T in 20 C |  | 0 |  | 0 |  | T in 25 C |  | 0
|  | 0 |  |  | 0 | 0.075725 | 0.46326 | 63.7139 | 0.076398 | 0.45495 | 62.557 | 0.077963 | 0.44928 | 61.326 | 0.081136 | 0.47345 | 62.927 | 0.084595 | 0.47967 | 61.9925 | 0.090166 | 0.49617 | 61.015 | 0.096674 | 0.51553 | 60.24 | 0.10397 | 0.53774 | 59.49 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.085696 | 0.46835 | 64.414 | 0.086458 | 0.46014 | 63.271 | 0.088229 | 0.47542 | 64.894 | 0.09182 | 0.48132 | 63.973 | 0.095734 | 0.48795 | 63.0625 | 0.10204 | 0.50492 | 62.091 | 0.1094 | 0.52462 | 61.302 | 0.11766 | 0.54717 | 60.5339 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.095647 | 0.47339 | 65.107 | 0.096497 | 0.48573 | 66.789 | 0.098475 | 0.48255 | 65.868 | 0.10248 | 0.48878 | 64.964 | 0.10685 | 0.49575 | 64.0715 | 0.11389 | 0.51325 | 63.115 | 0.12211 | 0.53339 | 62.327 | 0.13132 | 0.55583 | 61.4919 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.1056 | 0.49841 | 68.548 | 0.10654 | 0.49262 | 67.736 | 0.10872 | 0.4896 | 66.8301 | 0.11314 | 0.49611 | 65.939 | 0.11797 | 0.50333 | 65.0505 | 0.12574 | 0.52138 | 64.114 | 0.13481 | 0.54089 | 63.204 | 0.14498 | 0.56229 | 62.2059 |  | Correction factors |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.11557 | 0.50511 | 69.47 | 0.1166 | 0.49941 | 68.671 | 0.11899 | 0.49656 | 67.78 | 0.12383 | 0.50331 | 66.895 | 0.12911 | 0.51082 | 66.0185 | 0.13761 | 0.52841 | 64.979 | 0.14754 | 0.54711 | 63.93 | 0.15867 | 0.56841 | 62.8829 |  |  | 0.95504 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.12552 | 0.51174 | 70.381 | 0.12664 | 0.50607 | 69.586 | 0.12923 | 0.50344 | 68.7191 | 0.13449 | 0.51039 | 67.837 | 0.14022 | 0.51753 | 66.8855 | 0.14946 | 0.53434 | 65.7089 | 0.16025 | 0.55305 | 64.624 | 0.17233 | 0.57322 | 63.4149 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.13547 | 0.5187 | 71.3379 | 0.13668 | 0.5128 | 70.511 | 0.13948 | 0.50992 | 69.603 | 0.14515 | 0.51669 | 68.674 | 0.15134 | 0.52298 | 67.5905 | 0.16131 | 0.53995 | 66.3979 | 0.17295 | 0.55795 | 65.197 | 0.186 | 0.57105 | 63.1758 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.14542 | 0.52541 | 72.2609 | 0.14672 | 0.51949 | 71.432 | 0.14972 | 0.51622 | 70.463 | 0.15582 | 0.52162 | 69.329 | 0.16246 | 0.52775 | 68.2075 | 0.17316 | 0.54507 | 67.028 | 0.18565 | 0.55659 | 65.038 | 0.19966 | 0.568 | 62.8378 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.15539 | 0.53197 | 73.163 | 0.15677 | 0.52562 | 72.274 | 0.15999 | 0.5209 | 71.103 | 0.1665 | 0.52637 | 69.96 | 0.1736 | 0.53245 | 68.8145 | 0.18503 | 0.54451 | 66.9589 | 0.19838 | 0.5545 | 64.794 | 0.21335 | 0.60495 | 66.9258 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.16534 | 0.5383 | 74.034 | 0.16681 | 0.5301 | 72.8901 | 0.17023 | 0.52537 | 71.712 | 0.17716 | 0.53081 | 70.551 | 0.18471 | 0.5331 | 68.8985 | 0.19688 | 0.54357 | 66.843 | 0.21109 | 0.58742 | 68.641 | 0.22701 | 0.61222 | 67.7298 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.1753 | 0.54275 | 74.646 | 0.17685 | 0.53453 | 73.4991 | 0.18048 | 0.52979 | 72.316 | 0.18782 | 0.53245 | 70.7681 | 0.19583 | 0.53229 | 68.7935 | 0.20873 | 0.57207 | 70.348 | 0.22379 | 0.59423 | 69.436 | 0.24067 | 0.61937 | 68.5208 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.18525 | 0.54742 | 75.288 | 0.18689 | 0.53896 | 74.1081 | 0.19072 | 0.53288 | 72.738 | 0.19848 | 0.53199 | 70.708 | 0.20695 | 0.55787 | 72.0994 | 0.22057 | 0.57846 | 71.1341 | 0.2365 | 0.60094 | 70.22 | 0.25434 | 0.62636 | 69.2948 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.1952 | 0.55217 | 75.941 | 0.19693 | 0.54357 | 74.743 | 0.20097 | 0.53254 | 72.6911 | 0.20915 | 0.53129 | 70.6149 | 0.21806 | 0.56421 | 72.9195 | 0.23242 | 0.58502 | 71.94 | 0.2492 | 0.60771 | 71.011 | 0.268 | 0.63346 | 70.0797 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.20515 | 0.55702 | 76.6079 | 0.20697 | 0.54393 | 74.792 | 0.21121 | 0.5323 | 72.658 | 0.21981 | 0.56207 | 74.705 | 0.22918 | 0.57051 | 73.7334 | 0.24427 | 0.59163 | 72.753 | 0.2619 | 0.61456 | 71.8119 | 0.28166 | 0.64067 | 70.8778 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.2151 | 0.55968 | 76.974 | 0.21701 | 0.54397 | 74.798 | 0.22146 | 0.56093 | 76.5671 | 0.23047 | 0.56842 | 75.5499 | 0.2403 | 0.57697 | 74.5685 | 0.25612 | 0.59823 | 73.5649 | 0.27461 | 0.62142 | 72.614 | 0.29532 | 0.64905 | 71.8047 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.22505 | 0.56026 | 77.054 | 0.22705 | 0.54389 | 74.787 | 0.2317 | 0.5671 | 77.409 | 0.24113 | 0.57476 | 76.3921 | 0.25141 | 0.58349 | 75.4105 | 0.26797 | 0.60496 | 74.392 | 0.28731 | 0.6296 | 73.57 | 0.30899 | 0.65647 | 72.6257 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.235 | 0.56093 | 77.1469 | 0.23709 | 0.57582 | 79.177 | 0.24195 | 0.57271 | 78.174 | 0.2518 | 0.58079 | 77.193 | 0.26253 | 0.58982 | 76.2284 | 0.27982 | 0.61159 | 75.208 | 0.30002 | 0.63688 | 74.4199 | 0.32265 | 0.66527 | 73.5987 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.24495 | 0.58733 | 80.777 | 0.24713 | 0.58078 | 79.859 | 0.2522 | 0.57784 | 78.875 | 0.26246 | 0.58619 | 77.911 | 0.27365 | 0.59547 | 76.9594 | 0.29167 | 0.61928 | 76.154 | 0.31272 | 0.64495 | 75.363 | 0.33631 | 0.67394 | 74.5576 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.2549 | 0.59255 | 81.495 | 0.25717 | 0.58573 | 80.54 | 0.26244 | 0.58266 | 79.5331 | 0.27312 | 0.59115 | 78.571 | 0.28476 | 0.601 | 77.6735 | 0.30352 | 0.62574 | 76.948 | 0.32543 | 0.65232 | 76.224 | 0.34997 | 0.68637 | 75.9327 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.26486 | 0.59772 | 82.2059 | 0.26721 | 0.59087 | 81.2469 | 0.27269 | 0.58788 | 80.2451 | 0.28378 | 0.59638 | 79.2651 | 0.29588 | 0.60774 | 78.5444 | 0.31537 | 0.63191 | 77.706 | 0.33813 | 0.6626 | 77.425 | 0.36364 | 0.69322 | 76.6906 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.27481 | 0.60323 | 82.964 | 0.27725 | 0.59615 | 81.9729 | 0.28293 | 0.59306 | 80.952 | 0.29445 | 0.60228 | 80.05 | 0.307 | 0.61389 | 79.3404 | 0.32721 | 0.63788 | 78.441 | 0.35084 | 0.66887 | 78.158 | 0.3773 | 0.69983 | 77.4216 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.28474 | 0.60858 | 83.7 | 0.28727 | 0.60191 | 82.765 | 0.29316 | 0.59913 | 81.7811 | 0.30509 | 0.6094 | 80.996 | 0.31809 | 0.61973 | 80.0944 | 0.33904 | 0.64802 | 79.688 | 0.36351 | 0.67549 | 78.932 | 0.39093 | 0.70659 | 78.1696 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.29469 | 0.61376 | 84.412 | 0.29731 | 0.60767 | 83.557 | 0.3034 | 0.60526 | 82.617 | 0.31575 | 0.61557 | 81.816 | 0.32921 | 0.63002 | 81.4244 | 0.35089 | 0.65464 | 80.502 | 0.37622 | 0.68202 | 79.6949 | 0.4046 | 0.71358 | 78.9436 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.30464 | 0.61909 | 85.146 | 0.30735 | 0.61316 | 84.311 | 0.31365 | 0.61189 | 83.522 | 0.32641 | 0.62144 | 82.5959 | 0.34033 | 0.63623 | 82.2264 | 0.36274 | 0.66132 | 81.3231 | 0.38892 | 0.68908 | 80.52 | 0.41826 | 0.72057 | 79.7165 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.31459 | 0.62467 | 85.912 | 0.31739 | 0.61824 | 85.01 | 0.32389 | 0.61698 | 84.217 | 0.33707 | 0.63048 | 83.7971 | 0.35144 | 0.64196 | 82.9673 | 0.37459 | 0.66756 | 82.091 | 0.40163 | 0.6959 | 81.3169 | 0.43192 | 0.72741 | 80.4736 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.32452 | 0.63012 | 86.662 | 0.32741 | 0.62473 | 85.902 | 0.33412 | 0.6221 | 84.9161 | 0.34771 | 0.63594 | 84.523 | 0.36254 | 0.64741 | 83.6723 | 0.38641 | 0.67344 | 82.813 | 0.4143 | 0.70164 | 81.987 | 0.44556 | 0.7337 | 81.1696 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.33448 | 0.63498 | 87.331 | 0.33745 | 0.63001 | 86.628 | 0.34436 | 0.6314 | 86.186 | 0.35838 | 0.64172 | 85.292 | 0.37366 | 0.65328 | 84.4303 | 0.39826 | 0.67868 | 83.458 | 0.42701 | 0.7071 | 82.625 | 0.45922 | 0.73838 | 81.6865 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.34441 | 0.64188 | 88.2799 | 0.34747 | 0.63533 | 87.36 | 0.35459 | 0.63691 | 86.938 | 0.36902 | 0.64728 | 86.031 | 0.38475 | 0.65852 | 85.1074 | 0.41008 | 0.68421 | 84.138 | 0.43969 | 0.71261 | 83.2689 | 0.47285 | 0.74275 | 82.1705 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.35436 | 0.64714 | 89.003 | 0.35751 | 0.64458 | 88.6319 | 0.36483 | 0.64239 | 87.686 | 0.37968 | 0.65245 | 86.718 | 0.39587 | 0.66343 | 85.7424 | 0.42193 | 0.68953 | 84.7919 | 0.45239 | 0.71661 | 83.736 | 0.48652 | 0.74852 | 82.8085 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.36429 | 0.65649 | 90.289 | 0.36753 | 0.64992 | 89.3659 | 0.37506 | 0.64738 | 88.367 | 0.39032 | 0.65718 | 87.346 | 0.40696 | 0.66838 | 86.3824 | 0.43376 | 0.69346 | 85.275 | 0.46507 | 0.72101 | 84.251 | 0.50015 | 0.75397 | 83.4115 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.37424 | 0.66173 | 91.01 | 0.37756 | 0.65484 | 90.042 | 0.3853 | 0.65199 | 88.996 | 0.40098 | 0.66191 | 87.975 | 0.41808 | 0.67296 | 86.9743 | 0.44561 | 0.69706 | 85.718 | 0.47777 | 0.72592 | 84.8249 | 0.51381 | 0.75901 | 83.9695 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.38417 | 0.66659 | 91.678 | 0.38759 | 0.65944 | 90.675 | 0.39553 | 0.65657 | 89.621 | 0.41162 | 0.66663 | 88.603 | 0.42917 | 0.67664 | 87.4494 | 0.45743 | 0.70162 | 86.279 | 0.49045 | 0.73078 | 85.392 | 0.52745 | 0.76387 | 84.5075 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.39412 | 0.67121 | 92.3139 | 0.39762 | 0.66408 | 91.313 | 0.40577 | 0.66124 | 90.259 | 0.42229 | 0.67093 | 89.174 | 0.44029 | 0.68114 | 88.0314 | 0.46928 | 0.70624 | 86.847 | 0.50316 | 0.73534 | 85.925 | 0.54111 | 0.76525 | 84.6595 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.40405 | 0.67555 | 92.911 | 0.40764 | 0.66852 | 91.924 | 0.416 | 0.66611 | 90.923 | 0.43293 | 0.67555 | 89.788 | 0.45138 | 0.68551 | 88.5954 | 0.48111 | 0.7107 | 87.395 | 0.51584 | 0.73839 | 86.2819 | 0.55475 | 0.76461 | 84.5885 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.41398 | 0.67953 | 93.4579 | 0.41766 | 0.67297 | 92.535 | 0.42622 | 0.67084 | 91.569 | 0.44357 | 0.68007 | 90.389 | 0.46248 | 0.68994 | 89.1683 | 0.49293 | 0.71499 | 87.923 | 0.52851 | 0.73778 | 86.21 | 0.56838 | 0.76368 | 84.4855 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.42391 | 0.68295 | 93.928 | 0.42768 | 0.67779 | 93.198 | 0.43645 | 0.67483 | 92.113 | 0.45421 | 0.68447 | 90.974 | 0.47357 | 0.69422 | 89.7224 | 0.50476 | 0.71542 | 87.976 | 0.54119 | 0.73702 | 86.122 | 0.58202 | 0.76256 | 84.3625 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.43387 | 0.68696 | 94.4799 | 0.43772 | 0.68127 | 93.6769 | 0.44669 | 0.67857 | 92.624 | 0.46487 | 0.68823 | 91.4729 | 0.48469 | 0.69818 | 90.2334 | 0.5166 | 0.71479 | 87.8979 | 0.5539 | 0.73613 | 86.018 | 0.59568 | 0.76124 | 84.2164 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.4438 | 0.68988 | 94.881 | 0.44774 | 0.68417 | 94.076 | 0.45692 | 0.68181 | 93.0671 | 0.47551 | 0.69163 | 91.925 | 0.49578 | 0.69893 | 90.3303 | 0.52843 | 0.71398 | 87.799 | 0.56658 | 0.73496 | 85.881 | 0.60931 | 0.75982 | 84.0584 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.45373 | 0.69276 | 95.278 | 0.45776 | 0.68722 | 94.4949 | 0.46714 | 0.68504 | 93.507 | 0.48615 | 0.69492 | 92.363 | 0.50688 | 0.69839 | 90.2604 | 0.54026 | 0.71306 | 87.6859 | 0.57925 | 0.73372 | 85.736 | 0.62295 | 0.75823 | 83.8824 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.46366 | 0.69565 | 95.675 | 0.46778 | 0.69019 | 94.903 | 0.47736 | 0.68782 | 93.887 | 0.49679 | 0.69477 | 92.343 | 0.51797 | 0.69761 | 90.1593 | 0.55208 | 0.71178 | 87.5281 | 0.59193 | 0.73227 | 85.566 | 0.63658 | 0.7565 | 83.6915 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.47359 | 0.69849 | 96.065 | 0.4778 | 0.6928 | 95.2619 | 0.48759 | 0.68865 | 94.0001 | 0.50743 | 0.69444 | 92.298 | 0.52907 | 0.69671 | 90.0434 | 0.5639 | 0.71031 | 87.348 | 0.60461 | 0.73039 | 85.347 | 0.65022 | 0.76093 | 84.1815 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.48352 | 0.70157 | 96.489 | 0.48782 | 0.69401 | 95.429 | 0.49782 | 0.68844 | 93.971 | 0.51807 | 0.69401 | 92.241 | 0.54016 | 0.69551 | 89.8883 | 0.57573 | 0.70844 | 87.117 | 0.61729 | 0.73047 | 85.356 | 0.66385 | 0.77058 | 85.2495 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.49345 | 0.70297 | 96.681 | 0.49784 | 0.69383 | 95.403 | 0.50804 | 0.68811 | 93.9261 | 0.52872 | 0.6934 | 92.16 | 0.55126 | 0.69384 | 89.6723 | 0.58756 | 0.70694 | 86.933 | 0.62997 | 0.73951 | 86.412 | 0.67749 | 0.78018 | 86.3114 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.50338 | 0.703 | 96.685 | 0.50786 | 0.69357 | 95.3679 | 0.51826 | 0.68776 | 93.878 | 0.53936 | 0.69253 | 92.045 | 0.56235 | 0.69188 | 89.4193 | 0.59938 | 0.71181 | 87.532 | 0.64265 | 0.74845 | 87.457 | 0.69112 | 0.78968 | 87.3624 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.51329 | 0.7029 | 96.6719 | 0.51786 | 0.69326 | 95.325 | 0.52847 | 0.68724 | 93.8071 | 0.54997 | 0.69147 | 91.904 | 0.57342 | 0.69032 | 89.2173 | 0.61118 | 0.72028 | 88.574 | 0.6553 | 0.75743 | 88.506 | 0.70473 | 0.79915 | 88.4104 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.52323 | 0.70252 | 96.619 | 0.52788 | 0.69273 | 95.253 | 0.53869 | 0.68663 | 93.7241 | 0.56062 | 0.69013 | 91.726 | 0.58452 | 0.69393 | 89.6844 | 0.62301 | 0.72879 | 89.62 | 0.66798 | 0.76643 | 89.558 | 0.71837 | 0.80866 | 89.4624 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.53316 | 0.70185 | 96.5279 | 0.5379 | 0.69216 | 95.1739 | 0.54892 | 0.68588 | 93.622 | 0.57126 | 0.68892 | 91.565 | 0.59561 | 0.70208 | 90.7373 | 0.63483 | 0.73739 | 90.678 | 0.68066 | 0.77551 | 90.619 | 0.732 | 0.81832 | 90.5304 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.54307 | 0.70102 | 96.4139 | 0.5479 | 0.6915 | 95.083 | 0.55912 | 0.68506 | 93.51 | 0.58188 | 0.69074 | 91.8069 | 0.60668 | 0.71021 | 91.7883 | 0.64663 | 0.74598 | 91.734 | 0.69331 | 0.78457 | 91.678 | 0.74561 | 0.82799 | 91.6003 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.553 | 0.70015 | 96.293 | 0.55792 | 0.69085 | 94.9939 | 0.56935 | 0.68418 | 93.39 | 0.59252 | 0.69859 | 92.851 | 0.61778 | 0.71834 | 92.8393 | 0.65846 | 0.75453 | 92.7849 | 0.70599 | 0.79364 | 92.738 | 0.75924 | 0.83768 | 92.6723 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.56293 | 0.69924 | 96.168 | 0.56793 | 0.69011 | 94.892 | 0.57957 | 0.6882 | 93.939 | 0.60316 | 0.70645 | 93.895 | 0.62887 | 0.72643 | 93.8843 | 0.67028 | 0.76308 | 93.837 | 0.71867 | 0.80277 | 93.8049 | 0.77288 | 0.84756 | 93.7653 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.57284 | 0.69832 | 96.042 | 0.57793 | 0.69153 | 95.088 | 0.58978 | 0.69578 | 94.974 | 0.61378 | 0.71429 | 94.937 | 0.63994 | 0.73451 | 94.9294 | 0.68208 | 0.77177 | 94.905 | 0.73132 | 0.81193 | 94.8749 | 0.78649 | 0.85761 | 94.8773 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.58277 | 0.69918 | 96.161 | 0.58795 | 0.69903 | 96.118 | 0.6 | 0.70337 | 96.0091 | 0.62442 | 0.72215 | 95.981 | 0.65104 | 0.74264 | 95.9793 | 0.69391 | 0.78026 | 95.949 | 0.744 | 0.8211 | 95.946 | 0.80012 | 0.86761 | 95.9833 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.59268 | 0.70667 | 97.19 | 0.59795 | 0.70654 | 97.152 | 0.6102 | 0.71096 | 97.0451 | 0.63504 | 0.72997 | 97.021 | 0.66211 | 0.75075 | 97.0273 | 0.70571 | 0.78894 | 97.017 | 0.75665 | 0.83023 | 97.013 | 0.81373 | 0.87773 | 97.1033 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.60259 | 0.7141 | 98.213 | 0.60795 | 0.71401 | 98.1779 | 0.62041 | 0.71848 | 98.072 | 0.64566 | 0.73776 | 98.0569 | 0.67318 | 0.75882 | 98.0713 | 0.71751 | 0.79752 | 98.072 | 0.76931 | 0.83935 | 98.079 | 0.82734 | 0.8896 | 98.4162 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.61253 | 0.72159 | 99.242 | 0.61797 | 0.72143 | 99.199 | 0.63063 | 0.726 | 99.098 | 0.6563 | 0.74556 | 99.093 | 0.68428 | 0.767 | 99.1283 | 0.72934 | 0.80734 | 99.28 | 0.78198 | 0.85125 | 99.47 | 0.84097 | 0.90242 | 99.8352 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.62244 | 0.72894 | 100.254 | 0.62797 | 0.72878 | 100.21 | 0.64084 | 0.7335 | 100.122 | 0.66692 | 0.75372 | 100.1779 | 0.69535 | 0.77745 | 100.4783 | 0.74114 | 0.81827 | 100.624 | 0.79464 | 0.86331 | 100.879 | 0.85458 | 0.9129 | 100.9941 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.63235 | 0.73632 | 101.268 | 0.63797 | 0.73624 | 101.2349 | 0.65104 | 0.74167 | 101.237 | 0.67754 | 0.76374 | 101.509 | 0.70642 | 0.78785 | 101.8223 | 0.75294 | 0.82938 | 101.9901 | 0.80729 | 0.87544 | 102.296 | 0.86819 | 0.92313 | 102.1262 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.64226 | 0.74368 | 102.28 | 0.64797 | 0.74364 | 102.252 | 0.66124 | 0.75124 | 102.5441 | 0.68816 | 0.77366 | 102.8281 | 0.71749 | 0.79822 | 103.1632 | 0.76474 | 0.84048 | 103.355 | 0.81994 | 0.88768 | 103.7259 | 0.88179 | 0.93316 | 103.2352 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.65217 | 0.75103 | 103.291 | 0.65797 | 0.75101 | 103.266 | 0.67145 | 0.7608 | 103.8481 | 0.69878 | 0.78352 | 104.138 | 0.72857 | 0.80865 | 104.5113 | 0.77654 | 0.85157 | 104.718 | 0.8326 | 0.89992 | 105.157 | 0.8954 | 0.94222 | 104.2381 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.8954 | 0.94222 | 0 | 0
|  | 0 |  |  | 0 | 0.66208 | 0.75836 | 104.2999 | 0.66797 | 0.75947 | 104.429 | 0.68165 | 0.77053 | 105.1761 | 0.70939 | 0.7935 | 105.465 | 0.73964 | 0.81919 | 105.8732 | 0.78834 | 0.86277 | 106.0961 | 0.84525 | 0.91217 | 106.588 | 0.90901 | 0.95019 | 105.1191 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0.90901 | 0.95019
|  | 0 |  |  | 0 | 0.67199 | 0.76573 | 105.313 | 0.67797 | 0.76833 | 105.647 | 0.69186 | 0.78034 | 106.5161 | 0.72001 | 0.80348 | 106.7911 | 0.75071 | 0.82952 | 107.2082 | 0.80014 | 0.8741 | 107.489 | 0.8579 | 0.92478 | 108.062 | 0.92262 | 0.95745 | 105.9231 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.6819 | 0.77311 | 106.328 | 0.68797 | 0.77721 | 106.868 | 0.70206 | 0.79001 | 107.836 | 0.73063 | 0.81321 | 108.084 | 0.76178 | 0.83987 | 108.5462 | 0.81194 | 0.88581 | 108.9289 | 0.87055 | 0.93538 | 109.3 | 0.93622 | 0.96518 | 106.7781 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.69181 | 0.78041 | 107.332 | 0.69796 | 0.78635 | 108.126 | 0.71227 | 0.79943 | 109.121 | 0.74125 | 0.82318 | 109.4099 | 0.77285 | 0.85066 | 109.9402 | 0.82374 | 0.89778 | 110.401 | 0.88321 | 0.94217 | 110.094 | 0.94983 | 0.97274 | 107.614 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.70171 | 0.78844 | 108.4371 | 0.70794 | 0.79574 | 109.417 | 0.72245 | 0.80925 | 110.462 | 0.75185 | 0.83381 | 110.823 | 0.7839 | 0.8617 | 111.3671 | 0.83552 | 0.9101 | 111.916 | 0.89584 | 0.94812 | 110.789 | 0.96341 | 0.98209 | 108.6491 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.89584 | 0.94812 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.71162 | 0.79752 | 109.685 | 0.71794 | 0.80514 | 110.709 | 0.73265 | 0.82017 | 111.9531 | 0.76247 | 0.84487 | 112.292 | 0.79498 | 0.87318 | 112.8502 | 0.84732 | 0.92253 | 113.4439 | 0.90849 | 0.95331 | 111.395 | 0.97702 | 0.98856 | 109.3641 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0.90849 | 0.95331 | 1 | min | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.72153 | 0.80656 | 110.929 | 0.72794 | 0.81443 | 111.986 | 0.74286 | 0.83116 | 113.452 | 0.77309 | 0.85605 | 113.779 | 0.80605 | 0.88493 | 114.3691 | 0.85913 | 0.93546 | 115.0349 | 0.92114 | 0.96059 | 112.246 | 0.99063 | 0.99534 | 110.114 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.73142 | 0.81568 | 112.183 | 0.73792 | 0.82359 | 113.2459 | 0.75304 | 0.8421 | 114.946 | 0.78369 | 0.86731 | 115.275 | 0.8171 | 0.89694 | 115.9221 | 0.8709 | 0.9442 | 116.109 | 0.93377 | 0.96784 | 113.0929 | 1 | 1 | 110.63 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.74133 | 0.82472 | 113.4259 | 0.74792 | 0.83347 | 114.6039 | 0.76324 | 0.85305 | 116.4411 | 0.79431 | 0.87872 | 116.7919 | 0.82817 | 0.90938 | 117.5291 | 0.8827 | 0.94823 | 116.605 | 0.94642 | 0.97463 | 113.886 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.75122 | 0.8339 | 114.689 | 0.7579 | 0.84408 | 116.0639 | 0.77343 | 0.86426 | 117.9711 | 0.8049 | 0.89054 | 118.362 | 0.83922 | 0.92042 | 118.9562 | 0.89448 | 0.95166 | 117.027 | 0.95905 | 0.98238 | 114.7919 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.89448 | 0.95166 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.76111 | 0.84301 | 115.941 | 0.76788 | 0.85485 | 117.544 | 0.78361 | 0.87524 | 119.469 | 0.8155 | 0.90065 | 119.7069 | 0.85027 | 0.92989 | 120.1801 | 0.90626 | 0.95674 | 117.651 | 0.97168 | 0.98762 | 115.404 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0.90626 | 0.95674 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.77102 | 0.85201 | 117.1789 | 0.77788 | 0.86541 | 118.997 | 0.79382 | 0.884 | 120.665 | 0.82612 | 0.90971 | 120.9099 | 0.86134 | 0.93987 | 121.47 | 0.91806 | 0.96237 | 118.344 | 0.98433 | 0.99326 | 116.064 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.78092 | 0.86154 | 118.49 | 0.78786 | 0.87603 | 120.456 | 0.804 | 0.89254 | 121.831 | 0.83672 | 0.91912 | 122.161 | 0.87239 | 0.94718 | 122.4141 | 0.92984 | 0.96782 | 119.014 | 0.99696 | 0.99866 | 116.6939 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.79081 | 0.8714 | 119.8469 | 0.79783 | 0.88678 | 121.935 | 0.81418 | 0.90126 | 123.021 | 0.84732 | 0.92843 | 123.399 | 0.88344 | 0.95057 | 122.853 | 0.94161 | 0.97312 | 119.666 | 1 | 1 | 116.851 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.8007 | 0.88136 | 121.2159 | 0.80781 | 0.89784 | 123.4559 | 0.82437 | 0.90993 | 124.205 | 0.85791 | 0.93785 | 124.65 | 0.89449 | 0.95362 | 123.2471 | 0.95339 | 0.98058 | 120.583 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.89449 | 0.95362 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.81059 | 0.89133 | 122.588 | 0.81779 | 0.90663 | 124.6639 | 0.83455 | 0.91853 | 125.379 | 0.86851 | 0.94724 | 125.8979 | 0.90554 | 0.95647 | 123.6151 | 0.96517 | 0.98479 | 121.101 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0.90554 | 0.95647 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.82048 | 0.90154 | 123.992 | 0.82777 | 0.91495 | 125.809 | 0.84473 | 0.92752 | 126.606 | 0.87911 | 0.95665 | 127.149 | 0.91659 | 0.9616 | 124.2781 | 0.97695 | 0.9899 | 121.729 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.83037 | 0.91178 | 125.4 | 0.83775 | 0.92337 | 126.966 | 0.85492 | 0.93652 | 127.8341 | 0.88971 | 0.96492 | 128.2479 | 0.92764 | 0.96681 | 124.9521 | 0.98872 | 0.9951 | 122.368 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.88971 | 0.96492 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.84026 | 0.92219 | 126.831 | 0.84773 | 0.93179 | 128.124 | 0.8651 | 0.9453 | 129.032 | 0.90031 | 0.96816 | 128.679 | 0.93869 | 0.97206 | 125.6301 | 0.99993 | 0.99997 | 122.9669 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0.90031 | 0.96816 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.85013 | 0.93197 | 128.1759 | 0.85769 | 0.94005 | 129.259 | 0.87526 | 0.95424 | 130.253 | 0.91088 | 0.97073 | 129.021 | 0.94972 | 0.981 | 126.7851 | 0.99995 | 0.99998 | 122.969 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.86002 | 0.93972 | 129.2419 | 0.86767 | 0.94796 | 130.348 | 0.88545 | 0.96301 | 131.4501 | 0.92148 | 0.97322 | 129.352 | 0.96077 | 0.9836 | 127.122 | 1 | 1 | 122.971 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.86991 | 0.94739 | 130.2979 | 0.87765 | 0.95591 | 131.4399 | 0.89563 | 0.97176 | 132.645 | 0.93208 | 0.97718 | 129.878 | 0.97182 | 0.98808 | 127.7001 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.89563 | 0.97176 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.87979 | 0.95512 | 131.3609 | 0.8876 | 0.96386 | 132.534 | 0.90579 | 0.98151 | 133.975 | 0.94266 | 0.98186 | 130.5 | 0.98284 | 0.99279 | 128.3091 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0.90579 | 0.98151 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.88966 | 0.96293 | 132.4339 | 0.89756 | 0.97231 | 133.6959 | 0.91595 | 0.98574 | 134.552 | 0.95323 | 0.98692 | 131.173 | 0.99387 | 0.99733 | 128.8961 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.89756 | 0.97231 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.89955 | 0.97084 | 133.5229 | 0.90754 | 0.97644 | 134.264 | 0.92614 | 0.98681 | 134.699 | 0.96383 | 0.99461 | 132.195 | 1 | 1 | 129.241 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.89955 | 0.97084 | 0 | 0 | 1 | min | 0 | 0 | 0.90754 | 0.97644 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.90942 | 0.97665 | 134.321 | 0.9175 | 0.97909 | 134.6279 | 0.9363 | 0.98538 | 134.503 | 0.97441 | 0.99436 | 132.161 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0.90942 | 0.97665 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.91929 | 0.97934 | 134.691 | 0.92746 | 0.98177 | 134.996 | 0.94647 | 0.98761 | 134.8081 | 0.98498 | 0.99681 | 132.487 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.92916 | 0.98203 | 135.061 | 0.93742 | 0.9843 | 135.344 | 0.95663 | 0.99017 | 135.157 | 0.99556 | 0.99904 | 132.7839 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.93903 | 0.98456 | 135.41 | 0.94738 | 0.98663 | 135.665 | 0.96679 | 0.99248 | 135.472 | 0.99996 | 0.99999 | 132.9099 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.9489 | 0.98642 | 135.666 | 0.95734 | 0.98914 | 136.01 | 0.97695 | 0.99544 | 135.877 | 1 | 1 | 132.911 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.95877 | 0.98911 | 136.035 | 0.9673 | 0.99167 | 136.358 | 0.98712 | 0.99751 | 136.159 | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.96864 | 0.99385 | 136.687 | 0.97725 | 0.99479 | 136.786 | 0.99728 | 0.99947 | 136.4271 | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.97852 | 0.99523 | 136.8769 | 0.98721 | 0.9971 | 137.1039 | 0.99998 | 0.99999 | 136.4981 | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.98839 | 0.99729 | 137.16 | 0.99717 | 0.99941 | 137.422 | 1 | 1 | 136.499 | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 0.99824 | 0.99962 | 137.481 | 1 | 1 | 137.503 | 0.99657 | 0.99902 | 136.3657 | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 |  |  | 0 | 1 | 1 | 137.533 | 0.99997 | 1 | 137.503 | 1 | 1 | 136.499 | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[36 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0.89955 | 0.97084 | 0.90942 | 0.97665 |  |  | 0.89756 | 0.97231 | 0.90754 | 0.97644 |  |  | 0.89563 | 0.97176 | 0.90579 | 0.98151 |  |  | 0.88971 | 0.96492 | 0.90031 | 0.96816 |  |  | 0.89449 | 0.95362 | 0.90554 | 0.95647 |  |  | 0.89448 | 0.95166 | 0.90626 | 0.95674 |  |  | 0.89584 | 0.94812 | 0.90849 | 0.95331 |  |  | 0.8954 | 0.94222 | 0.90901 | 0.95019
[36 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0.89449 | 0.95362 | 0.90554 | 0.95647 |  |  | 0.89448 | 0.95166 | 0.90626 | 0.95674 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[38 empty] | -20 | #DIV/0! |  |  |  |  | -15 | #DIV/0! |  |  |  |  | -10 | #DIV/0! |  |  |  |  | -5 | #DIV/0! |  |  |  |  | 0 | #DIV/0! |  |  |  |  | 5 | #DIV/0! |  |  |  |  | 10 | 0.95504 |  |  |  |  | 15 | 0.95404 |  |  |  |  | 20 | #DIV/0! |  |  |  |  | 25 | #DIV/0!
[33 empty] | -20 and -15 | 0 | 0 | 0 | 0 | 0
[33 empty] | -15 and -10 | 0 | 0 | 0 | 0 | 0
[33 empty] | -10 and -5 | 0 | 0 | 0 | 0 | 0
[33 empty] | -5 and 0 | 0 | 0 | 0 | 0 | 0
[33 empty] | 0 and 5 | 0 | 0 | 0 | 0 | 0
[33 empty] | 5 and 10 | 0 | 0 | 0 | 0 | 0
[33 empty] | 10 and 15 | 10 | 15 | 25 | 0.95504 | 0.95404
[33 empty] | 15 and 20 | 0 | 0 | 0 | 0 | 0
[33 empty] | 20 and 25 | 0 | 0 | 0 | 0 | 0
[34 empty] | 10 | 15 |  | 0.95504 | 0.95404

## Part-load_Tout_Tin
Inlet Temp | -20 | C | Inlet Temp | -15 | C | Inlet Temp | -10 | C | Inlet Temp | -5 | C | Inlet Temp | 0 | C | Inlet Temp | 5 | C | Inlet Temp | 10 | C | Inlet Temp | 15 | C | Inlet Temp | 20 | C | Inlet Temp | 25 | C
Exhaust T | 429.91 | C | Exhaust T | 435.82 | C | Exhaust T | 441.42 | C | Exhaust T | 442.73 | C | Exhaust T | 443.8 | C | Exhaust T | 447.45 | C | Exhaust T | 451.53 | C | Exhaust T | 459.06 | C | Exhaust T | 466.21 | C | Exhaust T | 473.18 | C | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | X | 0 | 0
[30 empty] | T in | 10 | C |  | low | -20 | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20
[30 empty] | Part load | 0.9 |  |  | high | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25
Part load |  | Exh T (C) | Part load |  | Exh T (C) | Part load |  | Exh T (C) | Part load |  | Exh T (C) | Part load |  | Exh T (C) | Part load |  | Exh T (C) | Part load |  | Exh T (C) | Part load |  | Exh T (C) | Part load |  | Exh T (C) | Part load |  | Exh T (C) |  |  |  |  | T in -20 C |  | 0 |  |  |  | T in -15 C |  | 0 |  |  |  | T in -10 C |  | 0 |  |  |  | T in -5 C |  | 0 |  |  |  | T in 0 C |  | 0 |  |  |  | T in 5 C |  | 0 |  |  |  | T in 10 C |  | 0 |  |  |  | T in 15 C |  | 0 |  |  |  | T in 20 C |  | 0 |  |  |  | T in 25 C |  | 0
|  | 429.91 |  |  | 435.82 | 0.075725 | -31.07 | 410.35 | 0.076398 | -26.3 | 416.43 | 0.077963 | -21.28 | 422.52 | 0.081136 | -27.07 | 420.38 | 0.084595 | -20.81 | 430.72 | 0.090166 | -17.93 | 441.13 | 0.096674 | -16.34 | 449.87 | 0.10397 | -14.93 | 458.25 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.085696 | -32.05 | 409.37 | 0.086458 | -27.46 | 415.27 | 0.088229 | -30.72 | 413.08 | 0.09182 | -24.38 | 423.07 | 0.095734 | -18.35 | 433.18 | 0.10204 | -15.59 | 443.47 | 0.1094 | -13.92 | 452.29 | 0.11766 | -12.38 | 460.8 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.095647 | -33.15 | 408.27 | 0.096497 | -35.87 | 406.86 | 0.098475 | -27.53 | 416.27 | 0.10248 | -21.27 | 426.18 | 0.10685 | -15.35 | 436.18 | 0.11389 | -12.87 | 446.19 | 0.12211 | -11.28 | 454.93 | 0.13132 | -11.07 | 462.11 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.1056 | -40.71 | 400.71 | 0.10654 | -32.72 | 410.01 | 0.10872 | -24.47 | 419.33 | 0.11314 | -18.32 | 429.13 | 0.11797 | -12.5 | 439.03 | 0.12574 | -10.13 | 448.93 | 0.13481 | -10.4 | 455.81 | 0.14498 | -12.8 | 460.38 |  | Correction factors |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.11557 | -37.6 | 403.82 | 0.1166 | -29.72 | 413.01 | 0.11899 | -21.58 | 422.22 | 0.12383 | -15.45 | 432 | 0.12911 | -9.81 | 441.72 | 0.13761 | -9.56 | 449.5 | 0.14754 | -12.05 | 454.16 | 0.15867 | -14.54 | 458.64 |  |  | -9.1289 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.12552 | -34.49 | 406.93 | 0.12664 | -26.72 | 416.01 | 0.12923 | -18.78 | 425.02 | 0.13449 | -12.77 | 434.68 | 0.14022 | -8.76 | 442.77 | 0.14946 | -11.21 | 447.85 | 0.16025 | -13.81 | 452.4 | 0.17233 | -15.78 | 457.4 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.13547 | -31.94 | 409.48 | 0.13668 | -23.91 | 418.82 | 0.13948 | -15.66 | 428.14 | 0.14515 | -11.22 | 436.23 | 0.15134 | -10.07 | 441.46 | 0.16131 | -12.87 | 446.19 | 0.17295 | -15.26 | 450.95 | 0.186 | -13.43 | 459.75 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.14542 | -29.27 | 412.15 | 0.14672 | -21.27 | 421.46 | 0.14972 | -14.03 | 429.77 | 0.15582 | -12.35 | 435.1 | 0.16246 | -11.54 | 439.99 | 0.17316 | -14.53 | 444.53 | 0.18565 | -13.1 | 453.11 | 0.19966 | -11.06 | 462.12 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.15539 | -26.62 | 414.8 | 0.15677 | -19.24 | 423.49 | 0.15999 | -15.07 | 428.73 | 0.1665 | -13.46 | 433.99 | 0.1736 | -13.07 | 438.46 | 0.18503 | -12.88 | 446.18 | 0.19838 | -11.05 | 455.16 | 0.21335 | 8.53 | 481.71 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.16534 | -24.12 | 417.3 | 0.16681 | -20.21 | 422.52 | 0.17023 | -16.12 | 427.68 | 0.17716 | -14.83 | 432.62 | 0.18471 | -12.08 | 439.45 | 0.19688 | -11.12 | 447.94 | 0.21109 | 9.03 | 475.24 | 0.22701 | 11.91 | 485.09 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.1753 | -25.05 | 416.37 | 0.17685 | -21.24 | 421.49 | 0.18048 | -17.23 | 426.57 | 0.18782 | -14.55 | 432.9 | 0.19583 | -10.46 | 441.07 | 0.20873 | 9.44 | 468.5 | 0.22379 | 12.25 | 478.46 | 0.24067 | 15.21 | 488.39 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.18525 | -26.17 | 415.25 | 0.18689 | -22.33 | 420.4 | 0.19072 | -17.6 | 426.2 | 0.19848 | -13.02 | 434.43 | 0.20695 | 9.84 | 461.37 | 0.22057 | 12.55 | 471.61 | 0.2365 | 15.26 | 481.47 | 0.25434 | 18.21 | 491.39 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.1952 | -27.33 | 414.09 | 0.19693 | -23.58 | 419.15 | 0.20097 | -16.19 | 427.61 | 0.20915 | -11.66 | 435.79 | 0.21806 | 12.3 | 463.83 | 0.23242 | 15.02 | 474.08 | 0.2492 | 17.91 | 484.12 | 0.268 | 20.92 | 494.1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.20515 | -28.65 | 412.77 | 0.20697 | -22.22 | 420.51 | 0.21121 | -14.95 | 428.85 | 0.21981 | 8.16 | 455.61 | 0.22918 | 14.54 | 466.07 | 0.24427 | 17.31 | 476.37 | 0.2619 | 20.32 | 486.53 | 0.28166 | 23.32 | 496.5 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.2151 | -28.65 | 412.77 | 0.21701 | -21.02 | 421.71 | 0.22146 | 2.87 | 446.67 | 0.23047 | 9.92 | 457.37 | 0.2403 | 16.44 | 467.97 | 0.25612 | 19.43 | 478.49 | 0.27461 | 22.56 | 488.77 | 0.29532 | 23.92 | 497.1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.22505 | -27.52 | 413.9 | 0.22705 | -20.02 | 422.71 | 0.2317 | 4.62 | 448.42 | 0.24113 | 11.62 | 459.07 | 0.25141 | 18.07 | 469.6 | 0.26797 | 21.23 | 480.29 | 0.28731 | 22.67 | 488.88 | 0.30899 | 25.84 | 499.02 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.235 | -26.68 | 414.74 | 0.23709 | -1.83 | 440.9 | 0.24195 | 7.05 | 450.85 | 0.2518 | 13.7 | 461.15 | 0.26253 | 19.96 | 471.49 | 0.27982 | 23.08 | 482.14 | 0.30002 | 24.16 | 490.37 | 0.32265 | 26.05 | 499.23 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.24495 | -7 | 434.42 | 0.24713 | 1.35 | 444.08 | 0.2522 | 10.05 | 453.85 | 0.26246 | 16.51 | 463.96 | 0.27365 | 22.63 | 474.16 | 0.29167 | 23.33 | 482.39 | 0.31272 | 24.76 | 490.97 | 0.33631 | 26.4 | 499.58 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.2549 | -4.45 | 436.97 | 0.25717 | 4.35 | 447.08 | 0.26244 | 13.33 | 457.13 | 0.27312 | 19.79 | 467.24 | 0.28476 | 25.43 | 476.96 | 0.30352 | 25.38 | 484.44 | 0.32543 | 26.1 | 492.31 | 0.34997 | 21.25 | 494.43 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.26486 | -2.08 | 439.34 | 0.26721 | 6.9 | 449.63 | 0.27269 | 15.84 | 459.64 | 0.28378 | 22.59 | 470.04 | 0.29588 | 26.33 | 477.86 | 0.31537 | 27.66 | 486.72 | 0.33813 | 22.81 | 489.02 | 0.36364 | 23.51 | 496.69 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.27481 | 0 | 441.42 | 0.27725 | 9.08 | 451.81 | 0.28293 | 18.22 | 462.02 | 0.29445 | 24.36 | 471.81 | 0.307 | 27.97 | 479.5 | 0.32721 | 30.02 | 489.08 | 0.35084 | 25.19 | 491.4 | 0.3773 | 25.95 | 499.13 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.28474 | 2.15 | 443.57 | 0.28727 | 10.68 | 453.41 | 0.29316 | 19.55 | 463.35 | 0.30509 | 24.22 | 471.67 | 0.31809 | 29.93 | 481.46 | 0.33904 | 25.95 | 485.01 | 0.36351 | 26.93 | 493.14 | 0.39093 | 27.98 | 501.16 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.29469 | 4.59 | 446.01 | 0.29731 | 12.27 | 455 | 0.3034 | 20.65 | 464.45 | 0.31575 | 25.37 | 472.82 | 0.32921 | 25.11 | 476.64 | 0.35089 | 27.2 | 486.26 | 0.37622 | 28.69 | 494.9 | 0.4046 | 29.65 | 502.83 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.30464 | 6.64 | 448.06 | 0.30735 | 14.27 | 457 | 0.31365 | 21.11 | 464.91 | 0.32641 | 26.96 | 474.41 | 0.34033 | 26.45 | 477.98 | 0.36274 | 28.24 | 487.3 | 0.38892 | 29.76 | 495.97 | 0.41826 | 31.16 | 504.34 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.31459 | 8.39 | 449.81 | 0.31739 | 16.35 | 459.08 | 0.32389 | 23.2 | 467 | 0.33707 | 23.64 | 471.09 | 0.35144 | 28.3 | 479.83 | 0.37459 | 29.86 | 488.92 | 0.40163 | 31.02 | 497.23 | 0.43192 | 32.63 | 505.81 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.32452 | 10.14 | 451.56 | 0.32741 | 16.85 | 459.58 | 0.33412 | 25.49 | 469.29 | 0.34771 | 25.68 | 473.13 | 0.36254 | 30.79 | 482.32 | 0.38641 | 32.15 | 491.21 | 0.4143 | 33.71 | 499.92 | 0.44556 | 34.76 | 507.94 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.33448 | 11.13 | 452.55 | 0.33745 | 18.78 | 461.51 | 0.34436 | 21.61 | 465.41 | 0.35838 | 27.3 | 474.75 | 0.37366 | 32.41 | 483.94 | 0.39826 | 34.65 | 493.71 | 0.42701 | 36.27 | 502.48 | 0.45922 | 34.82 | 508 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.34441 | 12.4 | 453.82 | 0.34747 | 20.73 | 463.46 | 0.35459 | 23.41 | 467.21 | 0.36902 | 29.12 | 476.57 | 0.38475 | 34.72 | 486.25 | 0.41008 | 37.02 | 496.08 | 0.43969 | 37.23 | 503.44 | 0.47285 | 33.34 | 506.52 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.35436 | 14.25 | 455.67 | 0.35751 | 16.81 | 459.54 | 0.36483 | 25.02 | 468.82 | 0.37968 | 31.27 | 478.72 | 0.39587 | 37.35 | 488.88 | 0.42193 | 39.36 | 498.42 | 0.45239 | 35.69 | 501.9 | 0.48652 | 31.5 | 504.68 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.36429 | 10.46 | 451.88 | 0.36753 | 18.62 | 461.35 | 0.37506 | 27.09 | 470.89 | 0.39032 | 33.88 | 481.33 | 0.40696 | 39.84 | 491.37 | 0.43376 | 38.55 | 497.61 | 0.46507 | 34.18 | 500.39 | 0.50015 | 29.79 | 502.97 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.37424 | 12.23 | 453.65 | 0.37756 | 20.7 | 463.43 | 0.3853 | 29.73 | 473.53 | 0.40098 | 36.4 | 483.85 | 0.41808 | 41.07 | 492.6 | 0.44561 | 37.08 | 496.14 | 0.47777 | 32.48 | 498.69 | 0.51381 | 28.07 | 501.25 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.38417 | 14.47 | 455.89 | 0.38759 | 23.1 | 465.83 | 0.39553 | 32.16 | 475.96 | 0.41162 | 38.82 | 486.27 | 0.42917 | 39.97 | 491.5 | 0.45743 | 35.49 | 494.55 | 0.49045 | 30.84 | 497.05 | 0.52745 | 26.39 | 499.57 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.39412 | 16.69 | 458.11 | 0.39762 | 25.51 | 468.24 | 0.40577 | 34.56 | 478.36 | 0.42229 | 38.97 | 486.42 | 0.44029 | 38.58 | 490.11 | 0.46928 | 33.9 | 492.96 | 0.50316 | 29.21 | 495.42 | 0.54111 | 26.26 | 499.44 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.40405 | 19.42 | 460.84 | 0.40764 | 27.93 | 470.66 | 0.416 | 36.45 | 480.25 | 0.43293 | 37.63 | 485.08 | 0.45138 | 36.92 | 488.45 | 0.48111 | 32.22 | 491.28 | 0.51584 | 28.25 | 494.46 | 0.55475 | 26.95 | 500.13 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.41398 | 22.39 | 463.81 | 0.41766 | 30.26 | 472.99 | 0.42622 | 36.15 | 479.95 | 0.44357 | 36.21 | 483.66 | 0.46248 | 35.3 | 486.83 | 0.49293 | 30.57 | 489.63 | 0.52851 | 28.96 | 495.17 | 0.56838 | 27.69 | 500.87 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.42391 | 26.15 | 467.57 | 0.42768 | 32.41 | 475.14 | 0.43645 | 34.98 | 478.78 | 0.45421 | 34.96 | 482.41 | 0.47357 | 33.67 | 485.2 | 0.50476 | 30.79 | 489.85 | 0.54119 |  | 466.21 | 0.58202 | 28.33 | 501.51 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.43387 | 29.13 | 470.55 | 0.43772 | 31.61 | 474.34 | 0.44669 | 33.8 | 477.6 | 0.46487 | 33.49 | 480.94 | 0.48469 | 32.06 | 483.59 | 0.5166 | 31.49 | 490.55 | 0.5539 | 30.37 | 496.58 | 0.59568 | 29.02 | 502.2 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.4438 | 29.06 | 470.48 | 0.44774 | 30.69 | 473.42 | 0.45692 | 32.8 | 476.6 | 0.47551 | 32 | 479.45 | 0.49578 | 32.06 | 483.59 | 0.52843 | 32.17 | 491.23 | 0.56658 | 30.96 | 497.17 | 0.60931 | 29.61 | 502.79 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.45373 | 28.71 | 470.13 | 0.45776 | 30.14 | 472.87 | 0.46714 | 32.1 | 475.9 | 0.48615 | 30.91 | 478.36 | 0.50688 | 33.04 | 484.57 | 0.54026 | 32.99 | 492.05 | 0.57925 | 31.71 | 497.92 | 0.62295 | 30.36 | 503.54 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.46366 | 28.13 | 469.55 | 0.46778 | 29.58 | 472.31 | 0.47736 | 31.37 | 475.17 | 0.49679 | 31.86 | 479.31 | 0.51797 | 34.19 | 485.72 | 0.55208 | 34.25 | 493.31 | 0.59193 | 32.87 | 499.08 | 0.63658 | 31.33 | 504.51 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.47359 | 27.64 | 469.06 | 0.4778 | 29.01 | 471.74 | 0.48759 | 31.53 | 475.33 | 0.50743 | 32.88 | 480.33 | 0.52907 | 35.28 | 486.81 | 0.5639 | 35.33 | 494.39 | 0.60461 | 33.94 | 500.15 | 0.65022 | 30.48 | 503.66 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.48352 | 26.95 | 468.37 | 0.48782 | 29.34 | 472.07 | 0.49782 | 32.51 | 476.31 | 0.51807 | 33.81 | 481.26 | 0.54016 | 36.38 | 487.91 | 0.57573 | 36.52 | 495.58 | 0.61729 | 34.36 | 500.57 | 0.66385 | 28.38 | 501.56 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.49345 | 27.32 | 468.74 | 0.49784 | 30.38 | 473.11 | 0.50804 | 33.52 | 477.32 | 0.52872 | 34.84 | 482.29 | 0.55126 | 37.67 | 489.2 | 0.58756 | 37.53 | 496.59 | 0.62997 | 32.38 | 498.59 | 0.67749 | 26.32 | 499.5 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.50338 | 28.4 | 469.82 | 0.50786 | 31.34 | 474.07 | 0.51826 | 34.38 | 478.18 | 0.53936 | 35.86 | 483.31 | 0.56235 | 38.87 | 490.4 | 0.59938 | 36.54 | 495.6 | 0.64265 | 30.29 | 496.5 | 0.69112 | 24.22 | 497.4 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.51329 | 29.61 | 471.03 | 0.51786 | 32.3 | 475.03 | 0.52847 | 35.38 | 479.18 | 0.54997 | 36.86 | 484.31 | 0.57342 | 39.9 | 491.43 | 0.61118 | 34.6 | 493.66 | 0.6553 | 28.29 | 494.5 | 0.70473 | 22.22 | 495.4 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.52323 | 30.69 | 472.11 | 0.52788 | 33.32 | 476.05 | 0.53869 | 36.3 | 480.1 | 0.56062 | 37.98 | 485.43 | 0.58452 | 39.35 | 490.88 | 0.62301 | 32.67 | 491.73 | 0.66798 | 26.39 | 492.6 | 0.71837 | 20.24 | 493.42 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.53316 | 31.84 | 473.26 | 0.5379 | 34.32 | 477.05 | 0.54892 | 37.32 | 481.12 | 0.57126 | 39.01 | 486.46 | 0.59561 | 37.51 | 489.04 | 0.63483 | 30.8 | 489.86 | 0.68066 | 24.48 | 490.69 | 0.732 | 18.45 | 491.63 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.54307 | 32.91 | 474.33 | 0.5479 | 35.21 | 477.94 | 0.55912 | 38.25 | 482.05 | 0.58188 | 39.1 | 486.55 | 0.60668 | 35.74 | 487.27 | 0.64663 | 29 | 488.06 | 0.69331 | 22.65 | 488.86 | 0.74561 | 16.59 | 489.77 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.553 | 33.99 | 475.41 | 0.55792 | 36.1 | 478.83 | 0.56935 | 39.16 | 482.96 | 0.59252 | 37.32 | 484.77 | 0.61778 | 33.93 | 485.46 | 0.65846 | 27.23 | 486.29 | 0.70599 | 20.84 | 487.05 | 0.75924 | 14.76 | 487.94 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.56293 | 34.95 | 476.37 | 0.56793 | 36.97 | 479.7 | 0.57957 | 38.48 | 482.28 | 0.60316 | 35.58 | 483.03 | 0.62887 | 32.22 | 483.75 | 0.67028 | 25.51 | 484.57 | 0.71867 | 19.1 | 485.31 | 0.77288 | 12.82 | 486 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.57284 | 35.81 | 477.23 | 0.57793 | 37.18 | 479.91 | 0.58978 | 36.81 | 480.61 | 0.61378 | 33.85 | 481.3 | 0.63994 | 30.55 | 482.08 | 0.68208 | 23.8 | 482.86 | 0.73132 | 17.33 | 483.54 | 0.78649 | 10.89 | 484.07 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.58277 | 36.17 | 477.59 | 0.58795 | 35.49 | 478.22 | 0.6 | 35.18 | 478.98 | 0.62442 | 32.22 | 479.67 | 0.65104 | 28.91 | 480.44 | 0.69391 | 22.12 | 481.18 | 0.744 | 15.65 | 481.86 | 0.80012 | 8.9 | 482.08 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.59268 | 34.62 | 476.04 | 0.59795 | 33.96 | 476.69 | 0.6102 | 33.6 | 477.4 | 0.63504 | 30.6 | 478.05 | 0.66211 | 27.32 | 478.85 | 0.70571 | 20.48 | 479.54 | 0.75665 | 14 | 480.21 | 0.81373 | 6.98 | 480.16 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.60259 | 33.06 | 474.48 | 0.60795 | 32.34 | 475.07 | 0.62041 | 32.05 | 475.85 | 0.64566 | 29.09 | 476.54 | 0.67318 | 25.75 | 477.28 | 0.71751 | 18.85 | 477.91 | 0.76931 | 12.34 | 478.55 | 0.82734 | 4.73 | 477.91 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.61253 | 31.54 | 472.96 | 0.61797 | 30.87 | 473.6 | 0.63063 | 30.54 | 474.34 | 0.6563 | 27.55 | 475 | 0.68428 | 24.2 | 475.73 | 0.72934 | 17.07 | 476.13 | 0.78198 | 10.13 | 476.34 | 0.84097 | 2.4 | 475.58 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.62244 | 30.14 | 471.56 | 0.62797 | 29.33 | 472.06 | 0.64084 | 29.05 | 472.85 | 0.66692 | 26.02 | 473.47 | 0.69535 | 22.25 | 473.78 | 0.74114 | 15.06 | 474.12 | 0.79464 | 7.93 | 474.14 | 0.85458 | 0.52 | 473.7 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.63235 | 28.65 | 470.07 | 0.63797 | 27.96 | 470.69 | 0.65104 | 27.48 | 471.28 | 0.67754 | 24.14 | 471.59 | 0.70642 | 20.33 | 471.86 | 0.75294 | 13.16 | 472.22 | 0.80729 | 5.79 | 472 | 0.86819 | -1.23 | 471.95 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.64226 | 27.27 | 468.69 | 0.64797 | 26.53 | 469.26 | 0.66124 | 25.69 | 469.49 | 0.68816 | 22.29 | 469.74 | 0.71749 | 18.45 | 469.98 | 0.76474 | 11.32 | 470.38 | 0.81994 | 3.64 | 469.85 | 0.88179 | -3.08 | 470.1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.65217 | 25.83 | 467.25 | 0.65797 | 25.11 | 467.84 | 0.67145 | 23.84 | 467.64 | 0.69878 | 20.51 | 467.96 | 0.72857 | 16.65 | 468.18 | 0.77654 | 9.44 | 468.5 | 0.8326 | 1.5 | 467.71 | 0.8954 | -4.7 | 468.48 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.8954 | -4.7 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.66208 | 24.43 | 465.85 | 0.66797 | 23.54 | 466.27 | 0.68165 | 22.11 | 465.91 | 0.70939 | 18.8 | 466.25 | 0.73964 | 14.81 | 466.34 | 0.78834 | 7.54 | 466.6 | 0.84525 | -0.52 | 465.69 | 0.90901 | -6.22 | 466.96 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0.90901 | -6.22
|  | 429.91 |  |  | 435.82 | 0.67199 |  | 441.42 | 0.67797 | 21.88 | 464.61 | 0.69186 | 20.38 | 464.18 | 0.72001 | 17.08 | 464.53 | 0.75071 | 13.04 | 464.57 | 0.80014 | 5.54 | 464.6 | 0.8579 | -2.65 | 463.56 | 0.92262 | -6.21 | 466.97 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.6819 | 21.78 | 463.2 | 0.68797 | 20.31 | 463.04 | 0.70206 | 18.62 | 462.42 | 0.73063 | 15.4 | 462.85 | 0.76178 | 11.36 | 462.89 | 0.81194 | 3.54 | 462.6 | 0.87055 | -4.64 | 461.57 | 0.93622 | -4.92 | 468.26 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.69181 | 20.38 | 461.8 | 0.69796 | 18.71 | 461.44 | 0.71227 | 16.98 | 460.78 | 0.74125 | 13.72 | 461.17 | 0.77285 | 9.62 | 461.15 | 0.82374 | 1.48 | 460.54 | 0.88321 | -5.96 | 460.25 | 0.94983 | -3.91 | 469.27 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.70171 | 18.92 | 460.34 | 0.70794 | 17.02 | 459.75 | 0.72245 | 15.24 | 459.04 | 0.75185 | 11.98 | 459.43 | 0.7839 | 7.84 | 459.37 | 0.83552 | -0.63 | 458.43 | 0.89584 | -7.21 | 459 | 0.96341 | -1.91 | 471.27 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.89584 | -7.21 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.71162 | 17.34 | 458.76 | 0.71794 | 15.44 | 458.17 | 0.73265 | 13.65 | 457.45 | 0.76247 | 10.16 | 457.61 | 0.79498 | 5.89 | 457.42 | 0.84732 | -2.7 | 456.36 | 0.90849 | -7.54 | 458.67 | 0.97702 | -2.39 | 470.79 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0.90849 | -7.54 | 1 | min | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.72153 | 15.82 | 457.24 | 0.72794 | 13.89 | 456.62 | 0.74286 | 11.92 | 455.72 | 0.77309 | 8.41 | 455.86 | 0.80605 | 3.9 | 455.43 | 0.85913 | -4.98 | 454.08 | 0.92114 | -6.58 | 459.63 | 0.99063 | -1 | 472.18 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.73142 | 14.32 | 455.74 | 0.73792 | 12.39 | 455.12 | 0.75304 | 10.19 | 453.99 | 0.78369 | 6.71 | 454.16 | 0.8171 | 1.88 | 453.41 | 0.8709 | -6.76 | 452.3 | 0.93377 | -5.72 | 460.49 | 1 | 0 | 473.18 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.74133 | 12.83 | 454.25 | 0.74792 | 10.8 | 453.53 | 0.76324 | 8.52 | 452.32 | 0.79431 | 4.97 | 452.42 | 0.82817 | -0.19 | 451.34 | 0.8827 | -7.77 | 451.29 | 0.94642 | -4.39 | 461.82 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.75122 | 11.34 | 452.76 | 0.7579 | 9.15 | 451.88 | 0.77343 | 6.76 | 450.56 | 0.8049 | 3.04 | 450.49 | 0.83922 | -2.13 | 449.4 | 0.89448 | -8.66 | 450.4 | 0.95905 | -3.47 | 462.74 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.89448 | -8.66 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.76111 | 9.89 | 451.31 | 0.76788 | 7.54 | 450.27 | 0.78361 | 5 | 448.8 | 0.8155 | 1.28 | 448.73 | 0.85027 | -3.76 | 447.77 | 0.90626 | -8.37 | 450.69 | 0.97168 | -2.74 | 463.47 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0.90626 | -8.37 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.77102 | 8.46 | 449.88 | 0.77788 | 5.89 | 448.62 | 0.79382 | 3.58 | 447.38 | 0.82612 | -0.27 | 447.18 | 0.86134 | -5.53 | 446 | 0.91806 | -7.29 | 451.77 | 0.98433 | -1.71 | 464.5 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.78092 | 6.92 | 448.34 | 0.78786 | 4.22 | 446.95 | 0.804 | 2.1 | 445.9 | 0.83672 | -1.89 | 445.56 | 0.87239 | -7.08 | 444.45 | 0.92984 | -6.25 | 452.81 | 0.99696 | -0.34 | 465.87 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.79081 | 5.32 | 446.74 | 0.79783 | 2.53 | 445.26 | 0.81418 | 0.71 | 444.51 | 0.84732 | -3.46 | 443.99 | 0.88344 | -7.97 | 443.56 | 0.94161 | -5.03 | 454.03 | 1 | 0 | 466.21 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.8007 | 3.79 | 445.21 | 0.80781 | 0.76 | 443.49 | 0.82437 | -0.6 | 443.2 | 0.85791 | -5.03 | 442.42 | 0.89449 | -8.76 | 442.77 | 0.95339 | -4.03 | 455.03 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.89449 | -8.76 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.81059 | 2.23 | 443.65 | 0.81779 | -0.64 | 442.09 | 0.83455 | -2.04 | 441.76 | 0.86851 | -6.68 | 440.77 | 0.90554 | -9.5 | 442.03 | 0.96517 | -3.59 | 455.47 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0.90554 | -9.5 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.82048 | 0.61 | 442.03 | 0.82777 | -1.95 | 440.78 | 0.84473 | -3.5 | 440.3 | 0.87911 | -8.27 | 439.18 | 0.91659 | -8.51 | 443.02 | 0.97695 | -2.41 | 456.65 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.83037 | -0.92 | 440.5 | 0.83775 | -3.26 | 439.47 | 0.85492 | -5.02 | 438.78 | 0.88971 | -9.82 | 437.63 | 0.92764 | -7.29 | 444.24 | 0.98872 | -1.43 | 457.63 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.88971 | -9.82 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.84026 | -2.46 | 438.96 | 0.84773 | -4.58 | 438.15 | 0.8651 | -6.56 | 437.24 | 0.90031 | -10.56 | 436.89 | 0.93869 | -6.13 | 445.4 | 0.99993 | -0.04 | 459.02 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0.90031 | -10.56 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.85013 | -3.93 | 437.49 | 0.85769 | -5.8 | 436.93 | 0.87526 | -7.89 | 435.91 | 0.91088 | -11.35 | 436.1 | 0.94972 | -4.15 | 447.38 | 0.99995 | -0.07 | 458.99 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.86002 | -5.08 | 436.34 | 0.86767 | -7.06 | 435.67 | 0.88545 | -9.33 | 434.47 | 0.92148 | -12.12 | 435.33 | 0.96077 | -4.74 | 446.79 | 1 | 0 | 459.06 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.86991 | -6.28 | 435.14 | 0.87765 | -8.29 | 434.44 | 0.89563 | -10.85 | 432.95 | 0.93208 | -11.29 | 436.16 | 0.97182 | -3.67 | 447.86 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.89563 | -10.85 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.87979 | -7.51 | 433.91 | 0.8876 | -9.44 | 433.29 | 0.90579 | -12.45 | 431.35 | 0.94266 | -9.77 | 437.68 | 0.98284 | -2.41 | 449.12 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0.90579 | -12.45 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.88966 | -8.63 | 432.79 | 0.89756 | -10.91 | 431.82 | 0.91595 | -13.21 | 430.59 | 0.95323 | -8.62 | 438.83 | 0.99387 | -0.72 | 450.81 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.89756 | -10.91 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.89955 | -9.83 | 431.59 | 0.90754 | -11.71 | 431.02 | 0.92614 | -13.58 | 430.22 | 0.96383 | -6.25 | 441.2 | 1 | 0 | 451.53 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | min | 0.89955 | -9.83 | 0 | 0 | 1 | min | 0 | 0 | 0.90754 | -11.71 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.90942 | -10.71 | 430.71 | 0.9175 | -12.17 | 430.56 | 0.9363 | -13.76 | 430.04 | 0.97441 | -5.74 | 441.71 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0.90942 | -10.71 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.91929 | -10.97 | 430.45 | 0.92746 | -12.73 | 430 | 0.94647 | -11.83 | 431.97 | 0.98498 | -3.58 | 443.87 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.92916 | -11.31 | 430.11 | 0.93742 | -13.23 | 429.5 | 0.95663 | -9.56 | 434.24 | 0.99556 | -1.17 | 446.28 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.93903 | -11.68 | 429.74 | 0.94738 | -11.64 | 431.09 | 0.96679 | -7.24 | 436.56 | 0.99996 | 0.06 | 447.51 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.9489 | -11.66 | 429.76 | 0.95734 | -9.36 | 433.37 | 0.97695 | -6.06 | 437.74 | 1 | 0 | 447.45 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.95877 | -9.34 | 432.08 | 0.9673 | -7.05 | 435.68 | 0.98712 | -3.42 | 440.38 | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.96864 | -4.31 | 437.11 | 0.97725 | -5.59 | 437.14 | 0.99728 | -0.61 | 443.19 | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.97852 | -4.73 | 436.69 | 0.98721 | -3.05 | 439.68 | 0.99998 | 0.02 | 443.82 | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.98839 | -3.27 | 438.15 | 0.99717 | -0.73 | 442 | 1 | 0 | 443.8 | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 0.99824 | -0.61 | 440.81 | 1 | 0 | 442.73 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | min | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 429.91 |  |  | 435.82 | 1 | 0 | 441.42 | [25 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[36 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0.89955 | -9.83 | 0.90942 | -10.71 |  |  | 0.89756 | -10.91 | 0.90754 | -11.71 |  |  | 0.89563 | -10.85 | 0.90579 | -12.45 |  |  | 0.88971 | -9.82 | 0.90031 | -10.56 |  |  | 0.89449 | -8.76 | 0.90554 | -9.5 |  |  | 0.89448 | -8.66 | 0.90626 | -8.37 |  |  | 0.89584 | -7.21 | 0.90849 | -7.54 |  |  | 0.8954 | -4.7 | 0.90901 | -6.22
[36 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0.89449 | -8.76 | 0.90554 | -9.5 |  |  | 0.89448 | -8.66 | 0.90626 | -8.37 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[38 empty] | -20 | #DIV/0! |  |  |  |  | -15 | #DIV/0! |  |  |  |  | -10 | #DIV/0! |  |  |  |  | -5 | #DIV/0! |  |  |  |  | 0 | #DIV/0! |  |  |  |  | 5 | #DIV/0! |  |  |  |  | 10 | -9.1289 |  |  |  |  | 15 | -8.5241 |  |  |  |  | 20 | #DIV/0! |  |  |  |  | 25 | #DIV/0!
[33 empty] | -20 and -15 | 0 | 0 | 0 | 0 | 0
[33 empty] | -15 and -10 | 0 | 0 | 0 | 0 | 0
[33 empty] | -10 and -5 | 0 | 0 | 0 | 0 | 0
[33 empty] | -5 and 0 | 0 | 0 | 0 | 0 | 0
[33 empty] | 0 and 5 | 0 | 0 | 0 | 0 | 0
[33 empty] | 5 and 10 | 0 | 0 | 0 | 0 | 0
[33 empty] | 10 and 15 | 10 | 15 | 25 | -9.1289 | -8.5241
[33 empty] | 15 and 20 | 0 | 0 | 0 | 0 | 0
[33 empty] | 20 and 25 | 0 | 0 | 0 | 0 | 0
[34 empty] | 10 | 15 |  | -9.1289 | -8.5241

## GT calculator
Design values | GT LM6000 PF |  |  |  |  | Ref values | 41.945 | 8746.4 | 122.971 | 459.06 | [5 empty] | FUEL COMPOSITION
Inputs | [6 empty] | Power | HR | m out | T out |  | GT el power (MW) | 40.233 | [7 empty] | n out (kmol/s)
Calculations |  |  | Design | Actual |  |  | MW | kJ/kWh | kg/s | C | [5 empty] | METHANE | NATURAL GAS | M (kg/kmol) |  | n (kmol/s) | CO2 | H2O | N2 | O2 used
Outputs | T in | C | 15 | 10 |  |  | 1.0658 | 0.98673 | 1.051 | -7.53 |  | TOT fuel input (MW) | 98.5369 |  | N2 | 0% | 1.562% | 28.0134 | 0 | 0 | 0 | 0 | 0 | 0
| P atm | bar | 1.0132 | 1.0132 |  |  | 1 | 1 | 1 | 0 |  | TOT el output | 40.233 |  | CO2 | 0% | 0.1665% | 44.0095 | 0 | 0 | 0 | 0 | 0 | 0
| DP in | bar | 9.96 | 10 |  |  | 0.99994 | 1 | 0.99996 | 0.00448 |  | TOT eff | 40.83% |  | CH4 | 100% | 72.89% | 16.0425 | 16.0425 | 0.12273 | 0.12273 | 0.24546 | 0 | 0.24546
| DP out | bar | 14.95 | 15 |  |  | 0.99997 | 1 | 1 | 0.0080645 |  |  |  |  | C2H6 | 0% | 13.6% | 30.069 | 0 | 0 | 0 | 0 | 0 | 0
| Humidity |  | 0.6 | 0.6 |  |  | 1 | 1 | 1 | 0 | Influence of humidity hasn't been considered (yet) |  |  |  | C3H8 | 0% | 8.272% | 44.0956 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | ↓ | ↓ | ↓ | ↓ |  | aux GT1 (MW) | 0.08707 | 1 | C4H10 | 0% | 2.75% | 58.1222 | 0 | 0 | 0 | 0 | 0 | 0
| Generator η | 0.985 |  |  | Baseload correction |  | 1.0658 | 0.98677 | 1.0509 | -7.5175 |  | % aux misc 1 | 0.011506 |  | C5H12 | 0% | 0.667% | 72.1488 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Baseload ouput |  | 44.7033 | 8630.6822 | 129.2361 | 451.5425 |  |  |  |  | C6H14 | 0% | 0.091% | 86.1754 | 0 | 0 | 0 | 0 | 0 | 0
| Fuel | [10 empty] | net PW 1 (MW) | 39.683 | [5 empty] | 16.0425 | 0.12273 | 0.12273 | 0.24546 | 0 | 0.24546
| Type | 0 | 0=CH4; 1=NG |  | Load | 90% | Power | HR | m out | T out
| LHV | 50.047 | MJ/kg |  |  | ↓ | MW | kJ/kWh | kg/s | C
| P | 31.46 | bar |  | Part load correction |  | 0.9 | 1.0216 | 0.95504 | -9.1289 | [5 empty] | AIR COMPOSITION
| T | 25 | C |  | Part load output |  | 40.233 | 8816.9714 | 123.4258 | 442.4136
[18 empty] | M (kg/kmol) |  | n (kmol/s)
| NG correction factors |  |  |  | fake load | 13% |  | On or Off | 1 | [5 empty] | N2 | 77.39% |  | 28.0134 | 21.6793 | 3.256
| Power | 0.98786 | [12 empty] | O2 | 20.76% |  | 31.9988 | 6.6442 | 0.87359
| HR | 1.0038 |  |  | Outputs | [9 empty] | CO2 | 0.03% |  | 44.0095 | 0.013203 | 0.0012622
| m fuel in | 1.0474 |  |  | GT el power | MW | 40.233 | [7 empty] | H2O | 0.885% |  | 18.0153 | 0.15944 | 0.037234
| m out | 0.99515 |  |  | Gross LHV eff | % | 40.83% | [7 empty] | Ar | 0.932% |  | 39.948 | 0.37232 | 0.039212
| T out | 0.93216 |  |  | fuel flow | kg/s | 1.9689 | 98.5369 | [10 empty] | 28.8685 | 4.2073
[5 empty] | CO2 emissions | kg/s | 5.4568
[15 empty] | m FG | 123.4258 | kg/s
[15 empty] | m FUEL | 1.9689 | kg/s
[15 empty] | m AIR | 121.457 | kg/s
[15 empty] | n FG | 4.33 | kmol/s
[15 empty] | n FUEL | 0.12273 | kmol/s
[15 empty] | n AIR | 4.2073 | kmol/s
[15 empty] | M FG | 28.5049
FLUE GAS COMPOSITION
[16 empty] | n (kmol/s) | y (%) | M (kg/kmol) | m (kg/s)
[15 empty] | N2 | 3.256 | 75.2% | 28.0134 | 91.2102
[15 empty] | O2 | 0.62813 | 14.51% | 31.9988 | 20.0996
[15 empty] | CO2 | 0.12399 | 2.864% | 44.0095 | 5.4568
[15 empty] | H2O | 0.28269 | 6.529% | 18.0153 | 5.0928
[15 empty] | Ar | 0.039212 | 0.9056% | 39.948 | 1.5664
[16 empty] | 4.33 | 100% |  | 123.4258
4.33